Application No.:  359772

Equipment Category - Boiler

| 1. GENERAL INFORMATION |  |  | DATE: 4/16/2003 |
| --- | --- | --- | --- |
| a. manufacturer: Sellers Engineering |  |  |  |
| b. type: Fire-tube |  | c. model: 105E-395 HP |  |
| d. style: |  |  |  |
| e. applicable aqmd regulation xi rules: 1146 |  |  |  |
| f. cost: $100,000 (1999) source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 7 days/wk 50 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 359772 |
| --- | --- | --- | --- |
| A. FUNCTION: The boiler provided steam for a dye tank |  |  |  |
| B. maximum Heat Input: 16,500,000 BTU/hr |  | C. maximum throughput: |  |
| D. burner information: no.: 1 type: Air Pre-mix |  |  |  |
| e. primary fuel: Natural gas |  | f. other fuel: None |  |
| g. operating conditions: On/Off. The amount of time it was on was about 40% of the total time. |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 359772 |
| --- | --- | --- | --- |
| A. NAME: Damapong Textiles |  |  |  |
| B. ADDRESS: 700 W. Artesia Blvd CITY: Compton STATE: CA ZIP: 90220 |  |  |  |
| C. CONTACT PERSON: Out of Business |  | D. PHONE NO.: |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: 359772 |
| --- | --- | --- | --- | --- |
| A. AGENCY: `SCAQMD |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Kien Huynh |  |  | D. PHONE NO.: 909.396.2635 |  |
| E. PERMIT TO CONSTRUCT INFORMATION: P/C NO.: 359772 ISSUANCE DATE: 12/7/1999 check if no p/c |  |  |  |  |
| F. START-UP DATE: |  |  |  |  |
| G. PERMIT TO OPERATE INFORMATION: P/O NO.: F38078 ISSUANCE DATE: 3/16/2001 |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 359772 |
| --- | --- | --- | --- |
| A. PERMIT |  |  |  |
| A1. PERMIT LIMIT: NOx = 7 ppmv; CO = 50 ppmv; NH3 = 5 ppmv (dry basis corrected 3% O2) |  |  |  |
| A2. bact/lAer DETERMINATION: The BACT/LAER limits for CO and NH3 are as shown in Item 5A1. The 7 ppmv NOx limit was voluntarily requested by the applicant to reduce the facility's potential to emit. This NOx level was not considered as achieved in practice BACT for this size of boiler. |  |  |  |
| B. CONTROL TECHNOLOGY |  |  |  |
| B1. MANUFACTURER/SUPPLIER: Peerless |  |  |  |
| B2. TYPE: Selective Catalytic Reduction (SCR) |  |  |  |
| B3. DESCRIPTION: NOx is chemically reduced to N2 by the reducing agent NH3 in the presence of the catalyst. |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: 359776 ISSUANCE DATE: 12/7/1999 P/O NO.: F38079 ISSUANCE DATE: 3/16/2001 |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: 25 HP |  |  |  |
| B6. WARRANTY: 1-year parts. NOx, CO, NH3 guaranteed not to exceed 5, 50 and 10 ppmvd@3%O2, respectively. |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, SOx, and PM10 |  |  |  |
| B8. SECONDARY POLLUTANTS: None |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |
| B10. LIMITATIONS: See COMMENTS |  |  |  |
| B11. LOCATION OF PRIOR DEMONSTRATION & AGENCY: FACILITY: CONTACT PERSON: PHONE NO.: AGENCY: ADDRESS: CONTACT PERSON: PHONE NO.: |  |  |  |
| B12. OPERATING HISTORY: Unknown |  |  |  |
| B13. SOURCE TEST/PERFORMANCE DATA ANALYSIS: DATE OF SOURCE TEST: 12/12/2000 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: . OVERALL EFFICEINCY: PERFORMANCE DATA: |  |  |  |
| B14. SOURCE TEST CONDITIONS/PERFORMANCE DATA: Load Normal High O2, % (dry) 12.4 7.2 PPMVD@3%O2: NOx 4.2 2.9 CO 26 13 NH3 0.3 1.9 AQMD Methods 100.1 and 207.1 were used. Test durations were 1 hour at normal load (boiler cycling on and off to meet steam demand) and 30 minutes at high load. The source test protocol and the test report were approved by AQMD Monitoring & Source Test Engineering group. |  |  |  |
| C. COST |  |  |  |
| C1. CONTROL EQUIPMENT COST: check if installation cost is included in capital cost CAPITAL: $300,000 INSTALLATION: $ (1999) SOURCE OF COST DATA: |  |  |  |
| C2. ANNUAL OPERATIONAL/MAINTENANCE COST: $ (1999) SOURCE OF COST DATA: |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: None DATES: CAUSES: |  |  |  |
| D5. FREQUENCY OF MAINTENANCE: |  |  |  |

| 6. COMMENTS |  | App. No.: 359772 |
| --- | --- | --- |
| The boiler was either on at maximum load or off. Therefore, the ammonia injection rate was constant when the boiler was on. The original date of this listing was 12/21/1999. The listing was updated 3/13/2003 with P/O date and source test data. The facility went out of business, so a determination of continued reliability cannot be made. |  |  |