Application No.:  362616

Equipment Category - Boiler

| 1. GENERAL INFORMATION |  |  | DATE: 11/15/2002 |
| --- | --- | --- | --- |
| a. manufacturer: Superior |  |  |  |
| b. type: Fire-tube |  | c. model: 6X-2000-S150-LNDG210P-20 |  |
| d. style: |  |  |  |
| e. applicable aqmd rules: 1146 |  |  |  |
| f. cost: $85,000 () source of cost data: |  |  |  |
| g. operating schedule: 24 hrs/day 5 days/wk 52 wks/yr |  |  |  |

| 2. EQUIPMENT INFORMATION |  |  | App. No.: 362616 |
| --- | --- | --- | --- |
| A. FUNCTION: Process steam |  |  |  |
| B. maximum Heat Input: 16.4 MMBtu/hr |  | C. maximum throughput: |  |
| D. burner information: no.: 1 type: Low-NOx w/flue gas recirculation |  |  |  |
| e. primary fuel: Natural Gas |  | f. other fuel: |  |
| g. operating conditions: Load following |  |  |  |

| 3. COMPANY INFORMATION |  |  | App. No.: 362616 |  |
| --- | --- | --- | --- | --- |
| A. NAME: Y2K Textile, Inc. |  |  |  | B. SIC CODE: 2200 |
| C. ADDRESS: 2051 Raymer Avenue CITY: Fullerton STATE: CA ZIP: 92833 |  |  |  |  |
| D. CONTACT PERSON: Chris Park |  | E. PHONE NO.: 714-278-9797 |  |  |

| 4. PERMIT INFORMATION |  |  |  | App. No.: 362616 |
| --- | --- | --- | --- | --- |
| A. AGENCY: SCAQMD |  | B. application type: |  |  |
| C. AGENCY CONTACT PERSON: Kien Huynh |  |  | D. PHONE NO.: 909-396-2635 |  |
| E. PERMIT TO CONSTRUCT/OPERATE INFORMATION: P/C NO.: 362616 (A/N) ISSUANCE DATE: 1/5/2000 check if no p/c P/O NO.: F51838 ISSUANCE DATE: 5/1/2002 |  |  |  |  |
| F. START-UP DATE: February 2000 |  |  |  |  |

| 5. EMISSION INFORMATION |  |  | App. No.: 362616 |  |  |
| --- | --- | --- | --- | --- | --- |
| A. PERMIT |  |  |  |  |  |
| A1. PERMIT LIMIT: ppmvd@3%O2: NOx-11, CO-50, NH3-5 |  |  |  |  |  |
| A2. bact/lAer DETERMINATION: The CO and NH3 limits in the permit were BACT/LAER limits. The applicant offered the NOx limit of 11 ppmvd@3%O2 to reduce the facility potential to emit. |  |  |  |  |  |
| a3. BASIS OF THE BACT/LAER DETERMINATION: AQMD BACT Guidelines (4-10-98 update for boilers <16.7 MMBtu/hr) |  |  |  |  |  |
| ##### B. CONTROL TECHNOLOGY |  |  |  |  |  |
| B1. MANUFACTURER/SUPPLIER: Applied Utility Systems |  |  |  |  |  |
| B2. TYPE: Selective Catalytic Reduction (SCR) |  |  |  |  |  |
| B3. DESCRIPTION: NOx is chemically reduced to N2 by the reducing agent (NH3) in the presence of a catalyst. A fraction of the flue gas is bypassed around part of the heat exchange section of the boiler and re-mixed with the main flue gas stream upstream of the SCR catalyst. This is done to maintain the catalyst temperature above 460F, which is near the low end of the its operating range (350-650F). The ammonia injection rate is regulated based on fuel flow rate to the boiler, following a relationship that was developed at the time of initial emissions testing. |  |  |  |  |  |
| B4. CONTROL EQUIPMENT PERMIT APPLICATION DATA: P/C NO.: 362623 (A/N) ISSUANCE DATE: 1/5/2000 P/O NO.: F51840 ISSUANCE DATE: 5/1/2002 |  |  |  |  |  |
| B5. WASTE AIR FLOW TO CONTROL EQUIPMENT: FLOW RATE: ACTUAL CONTAMINANT LOADING: BLOWER HP: 10 |  |  |  |  |  |
| B6. WARRANTY: 1-year parts |  |  |  |  |  |
| B7. PRIMARY POLLUTANTS: NOx, CO, VOC, SOx, PM10 |  |  |  |  |  |
| B8. SECONDARY POLLUTANTS: NH3 |  |  |  |  |  |
| B9. SPACE REQUIREMENT: |  |  |  |  |  |
| B10. LIMITATIONS: |  |  |  | ###### B11. UNUSED |  |
| B12. OPERATING HISTORY: |  |  |  |  |  |
| ### B13. UNUSED |  | ### B14. UNUSED |  |  |  |
| ##### C. CONTROL EQUIPMENT COSTS |  |  |  |  |  |
| C1. CAPITAL COST: check if installation cost is included in EQUIPMENT cost EQUIPMENT: $85,000 INSTALLATION: $20,000 () SOURCE OF COST DATA: |  |  |  |  |  |
| C2. ANNUAL OPERATING COST: $ () SOURCE OF COST DATA: |  |  |  |  |  |
| D. DEMONSTRATION OF COMPLIANCE |  |  |  |  |  |
| D1. STAFF PERMFORMING FIELD EVALUATION: ENGINEER'S NAME: INSPECTOR'S NAME: DATE: |  |  |  |  |  |
| D2. COMPLIANCE DEMONSTRATION: |  |  |  |  |  |
| D3. VARIANCE: NO. OF VARIANCES: DATES: CAUSES: |  |  |  |  |  |
| D4. VIOLATION: NO. OF VIOLATIONS: DATES: CAUSES: |  |  |  |  |  |
| D5. MAINTENANCE REQUIREMENTS: Periodic refurbishment/replacement of catalyst. |  |  |  |  | D6. UNUSED |
| D7. SOURCE TEST/PERFORMANCE DATA RESULTS AND ANALYSIS: DATE OF SOURCE TEST: Dec 14-15, 2000 and 4/4/2001 CAPTURE EFFICIENCY: DESTRUCTION EFFICIENCY: OVERALL EFFICIENCY: SOURCE TEST/PERFORMANCE DATA: Date Dec 14-15, 2000 April 4, 2001 Test Low Fire Normal High Fire Normal High Fire NOx (ppmvd@3%O2) <2.2 2.0 2.9 1.8 1.7 CO (ppmvd@3%O2) <10.9 <9.5 11.4 2.8 7.8 NH3 (ppmvd@3%O2) 1.00 2.73 0.64 N/D 8.4 O2 (%, dry) 4.5 2.1 1.8 4.8 2.2 Heat Input (MMBtu/hr) 10.46 9.82 16.47 14.14 15.26 OPERATING CONDITIONS: TEST METHODS: The December 2000 test was accepted by AQMD's Monitoring & Source Test Engineering (MSTE) group. Heat input at low fire was incorrect in test report and was recalculated by (MSTE). The April 2001 test was an AQMD test. In the April test, the ammonia slip exceeded the permit limit. |  |  |  |  |  |

| 6. COMMENTS |  | App. No.: 362616 |
| --- | --- | --- |
| Along with this application the applicant submitted another application for an identical boiler at the same location (A/N 362618) also with an SCR system (A/N 362624). The ammonia exceedance in April 2001 may indicate difficulty in sustained compliance with a 5 ppm limit . The permit requires an annual check of ammonia emissions, and AQMD has requested the result for 2002. |  |  |