## Criteria Pollu. Emissions
DWP HARBOR STATION -- CRITERIA POLLUTANT EMISSIONS
NORMAL START-UP SCENARIO
Natural Gas Use by the Combustion Turbine
Device ID Number: | Combustion Turbines 1 through 5
Process Description:
No. of Devices: | Emissions are presented for one CT.
There are five CTs at this facility.
Process Equipment Description: | GE LM6000, Sprint 47.3 MW
Fuel Type: | Natural Gas
Process Units: | MMSCF
Control Equipment: | Selective Catalytic Reduction, CO Catalyst, and
water-steam injection for controlled operation.
Yearly Emis. Est. Equation: | Fy x EF
Max Hourly Emis. Est. Equation: | Fm x EF
Parameter Symbols/Names |  |  | Values
Fy = Total Yearly Amount of Fuel Burned (one CT) |  |  | NA | MMSCF
F1 = Fuel, Time 0 to 5 minutes |  |  | 0.01 | MMSCF
F2 = Fuel, Time 6 to 30 minutes |  |  | 0.103 | MMSCF
F3 = Fuel, Time 6 to 60 minutes |  |  | 0.227 | MMSCF
EF = Emission Factor |  |  | See below | lbs/MMSCF
Process Operation Schedule |  |  | 5 | minutes at no control
|  |  | 55 | minutes with water inection
| Initial (5 min.) | 55 minute | Full Control | Normal | Normal
Criteria | Emission | Emission | Emission | Start-Up | Start-Up Hrly
Species Name | Factor | Factor | Factor | Emissions | Emissions
| (lb/MMscf) | (lb/MMscf) | (lbs/MMscf) | (lbs/hour) | (grams/sec)
NOx | 309.75 | 98.28 | 19.64 | 25.41 | 3.2
CO | 185.85 | 35.07 | 14.39 | 9.82 | 1.24
VOC | 2.73 | 2.73 | 2.73 | 0.65 | 0.08
PM10 | 6.93 | 6.93 | 6.93 | 1.64 | 0.21
SO2 | 1.48 | 1.48 | 1.48 | 0.35 | 0.04
Note: Start-up emissions are for one CT, 5 minutes uncontrolled, 55 minutes water injection. After first hour full control.
There is no change in the emission factors for PM10, VOC and SO2 during controlled and uncontrolled operations.

## Air Toxics Emissions
DWP HARBOR STATION -- AIR TOXICS EMISSIONS
NORMAL START-UP SCENARIO
Natural Gas Use by the Combustion Turbines
Device ID Number: |  | Combustion Turbines 1 through 5
Process Description:
No. of Devices: |  | 5 (Note: Emissions are estimated for one combustion turbine) (1)
Process Equipment Description: |  | GE LM6000, Sprint 47.3 MW
Fuel Type: |  | Natural Gas
Process Units: |  | MMSCF
Control Equipment: |  | Selective Catalytic Reduction and CO Catalyst
Yearly Emis. Est. Equation: |  | Fy x EF
Max Hourly Emis. Est. Equation: |  | Fm x EF
Parameter Symbols/Names
Fy = Total Yearly Fuel Burned (one CT) 365 Starts |  |  | 86.505 | MMSCF
F1 = Fuel, Time 0 to 5 minutes |  |  | 0.01 | MMSCF
F2 = Fuel, Time 6 to 30 minutes |  |  | 0.103 | MMSCF
F3 = Fuel, Time 6 to 60 minutes |  |  | 0.227 | MMSCF
F3 = Fuel, Time 0 to 60 |  |  | 0.237 | lbs/MMSCF
EF = Emission Factor2,3 |  |  | See below | lbs/MMSCF
Process Operation Schedule |  |  | 5 | minutes at no control
|  |  | 55 | minutes with water inection
| Air Toxic | Emission | Houlry Max | Annual | Annual
Air Toxic | CAS Number | Factor | Emissions | Emissions | Emissions
|  | (lb/MMscf) | (lbs/hr) | (lbs/yr) | (tons/yr)
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
Ammonia | 7664417 | 7.25 | 1.7183 | 627.1612 | 0.31
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 1330207 | 0 | 0 | 0 | 0
1. Five new combustion turbines will be installed at the Harbor facility. The air toxics emissions
estimated are for each combustion turbine unit.
2. Mean Emission factors for all the air toxics except for ammonia are from the latest California Air
Resources Board's (CARB) air toxics emission data base. The emission factors were provided by
CARB to Parsons Engineering Science on 10/12/00.
3. The emissions are quantified for only those air toxics which are listed in Table 1 of the SCAQMD's
Rule 1401 (Amended August 2000).

## EF Criteria
DEVELOPMENT OF START-UP EMISSION FACTORS
NORMAL START-UP
FOR COMBUSTION TURBINES AT THE HARBOR PLANT
(Natural Gas Use by the Combustion Turbines)
1. The new combustion turbines (CTs) are GE LM6000 Sprint 47.3 MW (47,300 kW) turbine(1).
2. The heating input required is 8250 Btu/kW-hr (LHV), LM6000 GTG specifications(1).
3. The CTs will take 60 minutes to reach full power. (2)
4. Water injection will begin after 5 minutes. SCR and CO catalyst operation will begin at 60 minutes.(2)
5. The CTs will use natural gas with a HHV of 1050 Btu/scf (2).
6. Emission limits are 5 ppmv for oxides of nitrogen (NOx), 6 ppmv for carbon monoxide (CO),
2 ppmv for volatile organic compounds (VOC), and 5 ppmv for ammonia (NH3)(3) for controlled operations.
7. Emission limits are assumed to be at 15% O2.
8. Manufacturers value for VOC emissions used for all cases since AP-42 factors are less.
Calculate Maximum Firing Rate (MFR) for the CT in Btu/hr
Maximum Firing Rate = 47,300 kW X 8250 Btu/kW-hr
MFR | Size | Factor | LHV | HHV
(Btu/hr) | (kW) | (Btu/kW-hr) | (Btu/scf) | (Btu/scf)
390225000 | 47300 | 8250 | 953 | 1050
Maximum Hourly Fuel Consumption Rate (MMscf) = MFR/(LHV x 1,000,000)
Maximum Hourly Fuel Consumption Rate (MMscf/hr) = |  |  |  | 0.409 | MMscf/hr
Fuel Consumption during normal start-up
Fuel Burned in First 5 minutes = |  |  | 0.01 | MMscf (2)
Fuel Burned in from 6 to 25 minutes = |  |  | 0.103 | MMscf (2)
Fuel Burned from 6 to 60 minutes = Fuel Burned from 6 to 25 minutes X (55/25)
Fue Burned from 6 to 60 minutes = |  |  | 0.227 | MMscf
Time | Fuel Use | Heat Input
(minutes) | (MMscf) | (MMBtu)
0 to 5 | 0.01 | 10.5
6 to 30 | 0.103 | 108.2
6 to 60 | 0.227 | 238.4
Convert Emission Factors from lbs/MMBtu to lbs/MMscf
EF (lbs/Mgal) = EF (lbs/MMBtu) x HHV (Btu/scf)
ZERO TO FIVE MINUTES
| Pollutant | EF (5) | HHV | EF
|  | (lbs/MMBtu) | (Btu/scf) | (lbs/MMscf)
| NOx as NO2 | 0.295 | 1050 | 309.75
| CO | 0.177 | 1050 | 185.85
SIX TO 60 MINUTES
| Pollutant | EF (5) | HHV | EF
|  | (lbs/MMBtu) | (Btu/scf) | (lbs/MMscf)
| NOx as NO2 | 0.0936 | 1050 | 98.28
| CO | 0.0334 | 1050 | 35.07
AFTER FIRST HOUR (CONTROLLED OPERATIONS)
Calculate Molecular Weight of Natural Gas
| Compound | Mole% (4) | MW | Weighted MW
| methane | 94 | 16 | 15
| ethane | 3 | 30 | 0.9
| propane | 2 | 44 | 0.9
| CO2 | 1 | 44 | 0.4
| Total |  |  | 17.2
Convert Emission Limits (EL) from ppmv to lb/MMBtu for NOx, CO, VOC, and NH3 (controlled operations).
EL (lbs/MMBtu) = Exhaust Volume x Concentration x MW of Pollutant (6)
1,000,000 x 379
Exhaust Volume (DSCF/MMBtu) = 8710 DSCF/MMBtu x 20.9/(20.9 -%O2) (7)
Pollutant | Oxygen | Exhaust Vol | Conc. | MW |  | EL
| (%) | (DSCF/MMBtu) | (ppmv) | (lb/lb-mole) |  | (lb/MMBtu)
NOx (NO2)/water | 15 | 30854.0678 | 25 | 46 |  | 0.0936
NOx (NO2)/scr | 15 | 30854.0678 | 5 | 46 |  | 0.0187
CO | 15 | 30854.0678 | 6 | 28 |  | 0.0137
VOC (CH4) | 15 | 30854.0678 | 2 | 16 |  | 0.0026
NH3 | 15 | 30854.0678 | 5 | 17 |  | 0.0069
Convert Emission Limit (EL) in lb/MMBtu to Emission Factor in lb/MMscf, EF = EL x HHV (Btu/scf)
| Pollutant | EL | HHV | EF
|  | (lb/MMBtu) | (Btu/scf) | (lb/MMscf)
| NOx (NO2)/Water | 0.0936 | 1050 | 98.28
| NOx (NO2)/SCR | 0.0187 | 1050 | 19.64
| CO | 0.0137 | 1050 | 14.39
| VOC (CH4) | 0.0026 | 1050 | 2.73
| NH3 | 0.0069 | 1050 | 7.25
Emission Factors for PM10 and Sulfur Dioxide (SO2) all times
| Pollutant | Emission | HHV | Emission | Sulfur
|  | Factor | (Btu/scf) | Factor
|  | (lb/MMBtu) |  | (lb/MMscf) | (wt%)
| PM10 (5) | 0.0066 | 1050 | 6.93 | NA
| SO2 (5) | 0.94S | 1050 | 1.48 | 0.0015
Sulfur in Natural Gas (S)
WT% S = 100 x S in ppmv in natural gas x MW of S /(MW of Natural Gas x 106)
|  | Max.S in ppmv (4) | MW of S | MW of Natural Gas (4) | WT% S
|  | 8 | 32 | 17.2 | 0.0015
(1) Specification provided by LA DWP from Request for Proposal dated September 25, 2000 and
S & S Energy Products' Specifications sheet.
(2) Information provided by LA DWP in an e-mail to Krishna Nand on 11/01/00.
(3) Specifications from LA DWP (Generation - 2000 Project Overview)
(4) SCR Bid specification (no. 9628) from LA DWP. Natural gas LHV calculated to be 953 Btu/scf.
(5) Taken from AP-42, Section 3.1. Emission factors are all load emission factors
AP-42 Combustion Turbine Emission Factor Development Document, Table 3.4-1.
PM10 and Sulfur Dioxide emission factor is from AP-42, Table 3.1-2a. NOx factor derived from GE guarantee of 25 ppmv.
(6) Taken from SCAQMD Title V Technical Guidance Manual, page A-20, 1998.
(7) EPA Method 19, 40 CFR Part 60.

## Stack Calc
DEVELOPMENT OF THE STACK GAS FLOW RATE NORMAL START-UP
FOR THE COMBUSTION TURBINES AT THE HARBOR PLANT
(Natural Gasl Fuel Use by the Combustion Turbines)
1. The new combustion turbines (CTs) are GE LM6000 Sprints 47.3 MW (47,300 kW) turbine(1).
2. The heating input required is 8250 Btu/kW-hr (LHV), LM6000 GTG specifications(1).
3. The CTs will take 60 minutes to reach full power. (2)
4. Water injection will begin after 5 minutes. SCR and CO catylst operation will begin at 60 minutes.(2)
5. The CTs will use natural gas with a HHV of 1050 Btu/scf (2).
6. The assumed stack gas O2 content is 15%.
Calculate Maximum Firing Rate (MFR) for the CT in Btu/hr
Maximum Firing Rate = 47,300 kW X 8250 Btu/kW-hr
MFR | Size | Factor | LHV | HHV
(Btu/hr) | (kW) | (Btu/kW-hr) | (Btu/scf) | (Btu/scf)
390225000 | 47300 | 8250 | 953 | 1050
Maximum Hourly Fuel Consumption Rate (Mgal) = MFR/(LHV x 1,000,000)
Maximum Hourly Fuel Consumption Rate (MMscf/hr) = |  |  |  | 0.409 | MMscf/hr
Fuel Consumption during normal start-up
Fuel Burned in First 5 minutes = |  |  | 0.01 | MMscf (2)
Fuel Burned in from 6 to 25 minutes = |  |  | 0.103 | MMscf (2)
Fuel Burned from 6 to 60 minutes = Fuel Burned from 6 to 25 minutes X (55/25)
Fue Burned from 6 to 60 minutes = |  |  | 0.227 | MMscf
Time | Fuel Use | Heat Input
(minutes) | (MMscf) | (MMBtu)
0 to 5 | 0.01 | 10.5
6 to 30 | 0.103 | 108.2
6 to 60 | 0.227 | 238.4
Exhaust Volume (WSCF/MMBtu) = 10,610 WSCF/MMBtu x 20.9/(20.9 -%O2) (3)(4)
Stack Gas Flow Rate, ACF = |  | Stack Gas Flow (SCF) x |  | [Stack Gas Temp (oR)]
[Standard Temp (oR)]
oR = oF + 460
Standard Temp = 60 oF
Unit | Oxygen | Exhaust Vol | Heat Input | Exhaust Flow | Stack Temp. | Exhaust Flow | Exhaust Flow
| (%) | (WSCF/MMBtu) | (MMBtu/time) | (WSCF) | (oF) | (WACF) | (WACFS)
CT #1-5, 5min | 15 | 37584.5763 | 10.5 | 394638 | 420 | 667849 | 2226
CT #1-5, 6 to 30min | 15 | 37584.5763 | 108.2 | 4066651 | 420 | 6882025 | 4588
CT#1-5, 0 to 60min | 15 | 37584.5763 | 248.9 | 9354801 | 420 | 15831202 | 4398
Unit | Stack Inside Diameter(5) | Stack Exit Velocity | Stack Exit Velocity | Stack Inside Diameter | Stack Height(5) | Stack Height
| (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
CT #1-5, 5min | 10 | 28.34 | 8.64 | 3.05 | 110 | 33.53
CT #1-5, 6 to 30min | 10 | 58.42 | 17.81 | 3.05 | 110 | 33.53
CT#1-5, 0 to 60min | 10 | 56 | 17.07 | 3.05 | 110 | 33.53
(1) Specification provided by LA DWP from Request for Proposal dated September 25, 2000 and
and S & S Energy Products' Specifications sheet.
(2) SCR Bid specification (no. 9628) from LA DWP and information in an e-mail to Krishna Nand
received on 11/01/00.
(3) Taken from SCAQMD Title V Technical Guidance Manual, page A-20, 1998. Used natural gas F factor, wet.
(4) EPA Method 19, 40 CFR Part 60.
(5) Information regarding stack characteristics provided by DWP in an e-mail to Krishna Nand on 10/18/00.

## Air Toxics EF
CARB AIR TOXICS EMISSION FACTORS
COMBUSTION TURBINES -- NATURAL GAS
Air Toxics Emission factors are from California Air Resources Board's latest air toxics data
base. These emission factors are for combustion turbines equipped with SCR and CO
catalysts. The data were provided by CARB on 10/12/00 (fax from Kirk Rosenkranz to Krishna
Nand Tel. No. 916/322-7673).
Substance | Air Toxic | CAS No. | Rule 1401 | Mean Emission
Category |  |  | Listed Air | Factor
|  |  | Toxic (Y/N) | (lbs/MMSCF)
VOC | 1,3-Butadiene | 106990 | Y | 0.000127
SVOC | 2-Chloronaphthalene | 91587 | N | 2.72e-07
SVOC | 2-Methylnaphthalene | 91576 | N | 5.29e-06
PAH | Acenaphthene (PAH) | 83329 | N | 1.9e-05
PAH | Acenaphthylene (PAH) | 208968 | N | 1.47e-05
VOC | Acetaldehyde | 75070 | Y | 0.137
VOC | Acrolein | 107028 | Y | 0.0189
PAH | Anthracene (PAH) | 120127 | N | 3.38e-05
PAH | Benz(a)anthracene (PAH) | 56553 | Y | 2.26e-05
VOC | Benzene | 71432 | Y | 0.0133
PAH | Benzo(a)pyrene (PAH) | 50328 | Y | 1.39e-05
PAH | Benzo(b)fluoranthene (PAH) | 205992 | Y | 1.13e-05
PAH | Benzo(e)pyrene (PAH) | 192972 | N | 5.44e-07
PAH | Benzo(g,h,i)perylene (PAH) | 191242 | N | 1.37e-05
PAH | Benzo(k)fluoranthene (PAH) | 207089 | Y | 1.1e-05
PAH | Chrysene (PAH) | 218019 | Y | 2.52e-05
PAH | Dibenz(a,h)anthracene (PAH) | 53703 | Y | 2.35e-05
SVOC | Ethylbenzene | 100414 | Y | 0.0179
PAH | Fluoranthene (PAH) | 206440 | N | 4.32e-05
PAH | Fluorene (PAH) | 86737 | N | 5.8e-05
VOC | Formaldehyde | 50000 | Y | 0.917
VOC | Hexane | 110543 | Y | 0.259
PAH | Indeno(1,2,3-cd)pyrene (PAH) | 193395 | Y | 2.35e-05
PAH | Naphthalene (PAH) | 91203 | Y | 0.00166
SVOC | Perylene | 198550 | N | 7e-07
PAH | Phenanthrene (PAH) | 85018 | N | 0.000313
VOC | Propylene | 115071 | Y | 0.771
VOC | Propylene Oxide | 75569 | Y | 0.0478
PAH | Pyrene (PAH) | 129000 | N | 2.77e-05
VOC | Toluene | 108883 | Y | 0.071
VOC | Xylene(Total) | 1330207 | Y | 0.0261