## EF Criteria
DEVELOPMENT OF NOx AND NH3 EMISSIONS AND CREDITS
AND SO2 CONVERSION TO SO3 AND TO PM10
AT THE SCATTERGOOD PLANT
1. The Scattergood Plant has three boilers that will be fitted with SCR. (1)
2. Boilers No. 1 and No. 2 have a maximum natural gas consumption of 1685 mscfh each. (1)
3. Boiler No. 3 has a maximum natural gas consumption rate of 4140 mscfh. (1)
4. The stack gas flow rate for Boiler No.1 and Boiler No. 2 is 1,594,000 lbs/hr. (1)
5. The temperature for Boiler No. 1 and Boiler No. 2 is 294 oF. (1)
6. Boilers Nos.1 and 2 exhaust through a common stack, Stack No. 1. (1)
7. The stack gas flow rate for Boiler No. 3 is 3,641,000 lbs/hr. (1)
8. The temperature of Boiler No. 3 is 271 oF. (1)
9. Boiler No. 3 exhausts through a separate stack, Stack No. 2. (1)
10. The assumed stack gas O2 content is 3%.
11. The assumed stack gas molecular weight is 28.
12. The permitted NH3 conentration following SCR is 10 ppmv. Current NH3 from Units 1 and 2 is 20 ppmv.(2)
13. The permitted NOx concentration following SCR is 7 ppmv. (2)
14. The higher heating value of the natural gas is 1050 Btu/scf. (1)
Calculate Emission Rates Using AQMD Formula (3)
EF (lbs/MMBtu) = Exhaust Volume x Concentration x MW of Stack Gas
1,000,000 x 379
Calculate Exhaust Volume Using EPA Method 19, 40 CFR Part 60
Exhaust Volume (DSCF/MMBtu) = 8710 DSCF/MMBtu x 20.9/(20.9 -%O2)
1, Input per cent Oxygen.
2. Input pollutant concentration and fuel usage.
| Per Cent O2 | Exhaust Volume
(DSCF/MMBtu)
| 3 | 10169.7765
Fired Duty (MMBtu/hr) = Fuel (SCFH) x HHV (Btu/scf)
1000000
| Unit | Fuel | HHV | Fired Duty
|  | (SCFH) | (Btu/SCF) | (MMBtu/hr)
| Unit 1 | 1685000 | 1050 | 1769
| Unit 2 | 1685000 | 1050 | 1769
| Unit 3 | 4140000 | 1050 | 4347
Historical Emission Rates (5)
| UNIT | NOx | NOx | NOx | NOx | NOx
|  | (lbs) | (lbs) | (lbs) | (lbs) | (lbs/yr)
|  | 9-98 thru 12-98 | 1-99 thru 12-99 | 1-00 thru 8-00 | Total | Average
| Unit 1 | 4177 | 450780 | 183825 | 638782 | 319391
| Unit 2 | 444362 | 580880 | 476864 | 1502106 | 751053
| Unit 3 | 861796 | 669200 | 592791 | 2123787 | 1061894
|  | NH3 (ppm) | Total Stack Gas Flow (MMSCF) (5) | NH3 Total (lbs) | NH3 Average (lbs/yr)
| Unit 1 | 20 | 87548.85 | 78539.9 | 39269.95
| Unit 2 | 20 | 179934 | 161418.4 | 80709.2
| Unit 3 | NA | NA | NA | NA
[6 empty] | Hourly | Emissions | Annual (4) | Annual
Unit | Pollutant | Conc. | MW | EF | Firing | Emissions |  | Emissions | Emissions
|  | (ppmv) | (lb/lb-mole) | (lb/MMBtu) | (MMBTU/hr) | (lbs/hr) | (gm/sec) | (lbs/yr) | (tons/yr)
Unit 1 | NH3 | 10 | 17 | 0.0046 | 1769 | 8.14 | 1.03 | 71306 | 35.65
Unit 2 | NH3 | 10 | 17 | 0.0046 | 1769 | 8.14 | 1.03 | 71306 | 35.65
Stack 1 (Units 1&2) | NH3 | 10 | 17 | 0.0046 | 3538 | 16.28 | 2.06 | 142613 | 71.31
Unit 3 (Stack 2) | NH3 | 10 | 17 | 0.0046 | 4347 | 20 | 2.52 | 175200 | 87.6
Unit 1 | NOx | 7 | 46 | 0.0086 | 1769 | 15.21 | 1.92 | 133240 | 66.62
Unit 2 | NOx | 7 | 46 | 0.0086 | 1769 | 15.21 | 1.92 | 133240 | 66.62
Stack 1 (Units 1&2) | NOx | 7 | 46 | 0.0086 | 3538 | 30.42 | 3.84 | 266479 | 133.24
Unit 3 (Stack 2) | NOx | 7 | 46 | 0.0086 | 4347 | 37.38 | 4.71 | 327449 | 163.72
Unit 1 | SO2 | NA | 64 | 0.0014 | 1769 | 2.48 | 0.31 | 21725 | 10.86
Unit 2 | SO2 | NA | 64 | 0.0014 | 1769 | 2.48 | 0.31 | 21725 | 10.86
Stack 1 (Units 1&2) | SO2 | NA | 64 | 0.0014 | 3538 | 4.96 | 0.62 | 43450 | 21.73
Unit 3 (Stack 2) | SO2 | NA | 64 | 0.0014 | 4347 | 6.09 | 0.77 | 53348 | 26.67
Unit 1 | NH3 Slip PM10 | NA | 132.2 | 0.00014476 | 1769 | 0.26 | 0.03 | 2278 | 1.14
Unit 2 | NH3 Slip PM10 | NA | 132.2 | 0.00014476 | 1769 | 0.26 | 0.03 | 2278 | 1.14
Stack 1 (Units 1&2) | NH3 Slip PM10 | NA | 132.2 | 0.00014476 | 3538 | 0.52 | 0.06 | 4555 | 2.28
Unit 3 (Stack 2) | NH3 Slip PM10 | NA | 132.2 | 0.00014476 | 4347 | 0.63 | 0.08 | 5519 | 2.76
| Pollutant | Emission | Emission | Sulfur | Emission
|  | Factor | Factor |  | Factor
|  | (lb/MMscf) | (lb/MMscf) | (grains/dscf) | (lb/MMBtu)
| SO2 (6) | 0.6(S/S) | 1.42 | 4728 | 0.0014
Sulfur in Natural Gas (S)
WT% S = 100 x S in ppmv in natural gas x MW of S /(MW of Natural Gas x 106)
|  | S in ppmv (5) | MW of S | MW of Natural Gas (5) | S (grains/dscf)
|  | 8 | 32 | 17.2 | 4728
Calculate PM10 from Conversion of SO2 to ammonium sulfate
SO2 to SO3 = 5% molar conversion (8)
SO3 to ammonium sulfate: 1 mole SO3 = 1 mole of ammonium sulfate (8)
| SO2 | SO2 | SO3 | PM10 | PM10
| (lbs/BTU) | (lb-mole/MMBtu) | (lb-mole/MMBtu) | (lb/MMBtu) | (lbs/MMscf)
| 0.0014 | 2.1875e-05 | 1.0937e-06 | 0.00014459 | 0.152
Emission Credits Generated with SCR
| Unit | Max NOx prior to SCR | NOx PTE after SCR | Credit | Credit
|  | (lbs/yr) | (lbs/yr) | (lbs/yr) | (tons/yr)
| Unit 1 | 319391 | 133240 | 186151 | 93.0755
| Unit 2 | 751053 | 133240 | 751053 | 375.5265
| Stack 1 (Units 1 & 2) | 1070444 | 266479 | 803965 | 401.9825
| Unit 3 | 711894 | 327449 | 384445 | 192.2225
| Total |  |  |  | 594.205
| Unit | NH3 prior to SCR (lbs/yr) | NH3 PTE after SCR (lbs/yr) | NH3 Difference (lbs/yr)
| Unit 1 | 39269.95 | 71306 | 32036.05
| Unit 2 | 80709.2 | 71306 | -9403.2
| Unit 3 | 0 | 175200 | 175200
| Total |  |  | 197832.85
(1) SCR Bid Specification (No. 9628) provided by LA DWP.
(2) Specification from LA DWP (Generation - 2000 Projects Overview).
(3) SCAQMD Title V Technical Guidance Document, A-20, January 1998.
(4) Annual emissions = hourly emissions x 8760 hrs/yr.
(5) Emission data (Excel Worksheet) provided by LA DWP.
(6) Emission Factor from AP-42 Table 1.4-2. Natural gas emission factor based on
sulfur content of 2000 grains per MMscf. To convert factor to other sulfur content
multiply by the ration of sulfur in site natural gas to the sulfur in the EPA base gas.