## Criteria Pollu. Emissions
DWP VALLEY STATION -- CRITERIA POLLUTANT EMISSIONS
COMMISSIONING SCENARIO
Natural Gas Use by the Combustion Turbine
Device ID Number: | Combustion Turbine #1
Process Description:
No. of Devices: | 1
Process Equipment Description: | GE LM6000, Sprint 47.3 MW
Fuel Type: | Natural Gas
Process Units: | MMSCF
Control Equipment: | Selective Catalytic Reduction, CO Catalyst, and
water-steam injection for controlled operation.
Yearly Emis. Est. Equation: | Fy x EF
Max Hourly Emis. Est. Equation: | Fm x EF
Parameter Symbols/Names |  |  | Values
Fy = Total Yearly Amount of Fuel Burned (one CT) |  |  | NA | MMSCF
F1 = Fuel with no control, 0 to 10 hours. |  |  | 1.2 | MMSCF
F2 = Fuel with water injection, 11 to 60 hours. |  |  | 12.7 | MMSCF
F3 = Fuel with total control, 61 to 84 hours |  |  | 9.36 | MMSCF
EF = Emission Factor |  |  | See below | lbs/MMCF
Process Operation Schedule | 10 | hour at no control
| 50 | hours with water inection
| 0 to 10 hours | 11 to 60 hours | Remainder | Total | Total
Criteria | Emission | Emission | Emission | Hr. 0 to 10 | Hr.11 to 60
Species Name | Factor | Factor | Factor | Emissions | Emissions
| (lb/MMscf) | (lb/MMscf) | (lbs/MMscf) | (lbs) | (lbs)
NOx | 309.75 | 98.28 | 19.64 | 371.7 | 1248
CO | 185.85 | 35.07 | 14.39 | 223.02 | 445
VOC | 2.73 | 2.73 | 2.73 | 3.276 | 34.7
PM10 | 6.93 | 6.93 | 6.93 | 8.316 | 88
SO2 | 1.48 | 1.48 | 1.48 | 1.776 | 18.8
| Total | Hour 0 to 10 | Hour 11 -60 | Hour 61 to 84
Criteria | Hr. 61 to 84 | Hourly | Hourly | Hourly
Species Name | Emissions | Emissions | Emissions | Emissions
| (lbs) | (grams/sec) | (grams/sec) | (grams/sec)
NOx | 183.8304 | 4.69 | 3.15 | 0.97
CO | 134.6904 | 2.81 | 1.12 | 0.71
VOC | 25.5528 | 0.04 | 0.09 | 0.13
PM10 | 64.8648 | 0.1 | 0.22 | 0.34
SO2 | 13.8528 | 0.02 | 0.05 | 0.07

## Air Toxics Emissions
DWP VALLEY STATION --AIR TOXIC POLLUTANT EMISSIONS
COMMISSIONING SCENARIO
Natural Gas Use by the Combustion Turbine
Device ID Number: | Combustion Turbine #1
Process Description:
No. of Devices: | 1
Process Equipment Description: | GE LM6000, Sprint 47.3 MW
Fuel Type: | Natural Gas
Process Units: | MMSCF
Control Equipment: | Selective Catalytic Reduction, CO Catalyst, and
water-steam injection for controlled operation.
Yearly Emis. Est. Equation: | Fy x EF
Max Hourly Emis. Est. Equation: | Fm x EF
Parameter Symbols/Names |  |  | Values
Fy = Total Yearly Amount of Fuel Burned (one CT) |  |  | NA | MMSCF
F1 = Fuel with no control, 0 to 10 hours. |  |  | 1.2 | MMSCF
F2 = Fuel with water injection, 11 to 60 hours. |  |  | 12.7 | MMSCF
F3 = Fuel with total control, 61 to 84 hours |  |  | 9.36 | MMSCF
EF = Emission Factor |  |  | See below | lbs/MMCF
Process Operation Schedule | 10 | hour at no control
| 50 | hours with water inection
| Air Toxic | 0 to 84 hours | Total | Total | Total
Air Toxic | CAS Number | Emission | Hr. 0 to 10 | Hr.11 to 60 | Hr. 61 to 84
|  | Factor (1) | Emissions | Emissions | Emissions
|  | (lb/MMscf) | (lbs) | (lbs) | (lbs)
1,3-Butadiene | 106990 | 0.000127 | 0.0001524 | 0.0016129 | 0.0011887
Acetaldehyde | 75070 | 0.137 | 0.1644 | 1.7399 | 1.2823
Acrolein | 107028 | 0.0189 | 0.02268 | 0.24003 | 0.1769
Ammonia | 7664417 | 7.25 | 8.7 | 92.075 | 67.86
Benz(a)anthracene (PAH) | 56553 | 2.26e-05 | 2.712e-05 | 0.00028702 | 0.00021154
Benzene | 71432 | 0.0133 | 0.01596 | 0.16891 | 0.12449
Benzo(a)pyrene (PAH) | 50328 | 1.39e-05 | 1.668e-05 | 0.00017653 | 0.0001301
Benzo(b)fluoranthene (PAH) | 205992 | 1.13e-05 | 1.356e-05 | 0.00014351 | 0.00010577
Benzo(k)fluoranthene (PAH) | 207089 | 1.1e-05 | 1.32e-05 | 0.0001397 | 0.00010296
Chrysene (PAH) | 218019 | 2.52e-05 | 3.024e-05 | 0.00032004 | 0.00023587
Dibenz(a,h)anthracene (PAH) | 53703 | 2.35e-05 | 2.82e-05 | 0.00029845 | 0.00021996
Ethylbenzene | 100414 | 0.0179 | 0.02148 | 0.22733 | 0.16754
Formaldehyde | 50000 | 0.917 | 1.1004 | 11.6459 | 8.5831
Hexane | 110543 | 0.259 | 0.3108 | 3.2893 | 2.4242
Indeno(1,2,3-cd)pyrene (PAH) | 193395 | 2.35e-05 | 2.82e-05 | 0.00029845 | 0.00021996
Naphthalene (PAH) | 91203 | 0.00166 | 0.001992 | 0.021082 | 0.015538
Propylene | 115071 | 0.771 | 0.9252 | 9.7917 | 7.2166
Propylene Oxide | 75569 | 0.0478 | 0.05736 | 0.60706 | 0.44741
Toluene | 108883 | 0.071 | 0.0852 | 0.9017 | 0.66456
Xylene(Total) | 1330207 | 0.0261 | 0.03132 | 0.33147 | 0.2443
| Air Toxic | Total | Hour 0 to 10 | Hour 11 -60 | Hour 61 to 84
Air Toxic | CAS Number | Hr. 0 to 84 | Hourly | Hourly | Hourly
|  | Emissions | emissions | Emissions | Emissions
|  | (lbs) | (grams/sec) | (grams/sec) | (grams/sec)
1,3-Butadiene | 106990 | 0.002954 | 1.9219e-06 | 4.0681e-06 | 6.2463e-06
Acetaldehyde | 75070 | 3.1866 | 0.0020733 | 0.0043884 | 0.0067381
Acrolein | 107028 | 0.43961 | 0.00028602 | 0.00060541 | 0.00092957
Ammonia | 7664417 | 168.635 | 0.10972 | 0.23223 | 0.35658
Benz(a)anthracene (PAH) | 56553 | 0.00052568 | 3.4201e-07 | 7.2393e-07 | 1.1115e-06
Benzene | 71432 | 0.30936 | 0.00020127 | 0.00042603 | 0.00065414
Benzo(a)pyrene (PAH) | 50328 | 0.00032331 | 2.1035e-07 | 4.4525e-07 | 6.8365e-07
Benzo(b)fluoranthene (PAH) | 205992 | 0.00026284 | 1.7101e-07 | 3.6196e-07 | 5.5577e-07
Benzo(k)fluoranthene (PAH) | 207089 | 0.00025586 | 1.6647e-07 | 3.5235e-07 | 5.4102e-07
Chrysene (PAH) | 218019 | 0.00058615 | 3.8136e-07 | 8.0721e-07 | 1.2394e-06
Dibenz(a,h)anthracene (PAH) | 53703 | 0.00054661 | 3.5563e-07 | 7.5276e-07 | 1.1558e-06
Ethylbenzene | 100414 | 0.41635 | 0.00027089 | 0.00057338 | 0.00088038
Formaldehyde | 50000 | 21.3294 | 0.013877 | 0.029374 | 0.045101
Hexane | 110543 | 6.0243 | 0.0039195 | 0.0082963 | 0.012738
Indeno(1,2,3-cd)pyrene (PAH) | 193395 | 0.00054661 | 3.5563e-07 | 7.5276e-07 | 1.1558e-06
Naphthalene (PAH) | 91203 | 0.038612 | 2.5121e-05 | 5.3173e-05 | 8.1644e-05
Propylene | 115071 | 17.9335 | 0.011668 | 0.024697 | 0.03792
Propylene Oxide | 75569 | 1.1118 | 0.00072337 | 0.0015311 | 0.002351
Toluene | 108883 | 1.6515 | 0.0010745 | 0.0022743 | 0.003492
Xylene(Total) | 1330207 | 0.60709 | 0.00039498 | 0.00083604 | 0.0012837
1. Controlled and Uncontrolled Air Toxics Emission Factor are identical.

## EF Criteria
DEVELOPMENT OF COMMISSIONING EMISSION FACTORS
FOR COMBUSTION TURBINES AT THE VALLEY PLANT
(Natural Gas Use by the Combustion Turbine)
1. The new combustion turbine (CT) is a GE LM6000 Sprint 47.3 MW (47,300 kW) turbine(1).
2. The heating input required is 8250 Btu/kW-hr (LHV), LM6000 GTG specifications(1).
3. The CT will reach full power in 24 hours. (2)
4. Water injection will begin after 10 hours. SCR and CO catylst operation will begin at 61 hours.(2)
5. The CT will use natural gas with a HHV of 1050 Btu/scf (2).
6. Emission limits are 5 ppmv for oxides of nitrogen (NOx), 6 ppmv for carbon monoxide (CO),
2 ppmv for volatile organic compounds (VOC), and 5 ppmv for ammonia (NH3)(3) for controlled operations.
7. Emission limits are assumed to be at 15% O2.
Calculate Maximum Firing Rate (MFR) for the CT in Btu/hr
Maximum Firing Rate = 47,300 kW X 8250 Btu/kW-hr
MFR | Size | Factor | LHV | HHV
(Btu/hr) | (kW) | (Btu/kW-hr) | (Btu/scf) | (Btu/scf)
390225000 | 47300 | 8250 | 953 | 1050
Maximum Hourly Fuel Consumption Rate (MMscf) = MFR/(LHV x 1,000,000)
Maximum Hourly Fuel Consumption Rate (MMscf/hr) = |  |  |  | 0.409 | MMscf/hr
Fuel Consumption during test
Time | Fuel Use (2) | Fuel
(hours) | (MMscf) | (MMBtu)
0 to 10 | 1.2 | 1260
11 to 60 | 12.7 | 13335
61 to 84 | 9.36 | 9828
Convert Emission Factors from lbs/MMBtu to lbs/MMscf
EF (lbs/MMscf) = EF (lbs/MMBtu) x HHV (Btu/scf)
ZERO TO TEN HOURS
| Pollutant | EF (5) | HHV | EF
|  | (lbs/MMBtu) | (Btu/scf) | (lbs/MMscf)
| NOx as NO2 | 0.295 | 1050 | 309.75
| CO | 0.177 | 1050 | 185.85
ELEVEN TO SIXTY HOURS
| Pollutant | EF (5) | HHV | EF
|  | (lbs/MMBtu) | (Btu/scf) | (lbs/MMscf)
| NOx as NO2 | 0.0936 | 1050 | 98.28
| CO | 0.0334 | 1050 | 35.07
Calculate Molecular Weight of Natural Gas
| Compound | Mole% (4) | MW | Weighted MW
| methane | 94 | 16 | 15
| ethane | 3 | 30 | 0.9
| propane | 2 | 44 | 0.9
| CO2 | 1 | 44 | 0.4
| Total |  |  | 17.2
Convert Emission Limits (EL) from ppmv to lb/MMBtu for NOx, CO, VOC, and NH3 (controlled operations).
EL (lbs/MMBtu) = Exhaust Volume x Concentration x MW of Pollutant (6)
1,000,000 x 379
Exhaust Volume (DSCF/MMBtu) = 8710 DSCF/MMBtu x 20.9/(20.9 -%O2) (7)
Pollutant | Oxygen | Exhaust Vol | Conc. | MW |  | EL
| (%) | (DSCF/MMBtu) | (ppmv) | (lb/lb-mole) |  | (lb/MMBtu)
NOx (NO2)/water | 15 | 30854.0678 | 25 | 46 |  | 0.0936
NOx (NO2)/scr | 15 | 30854.0678 | 5 | 46 |  | 0.0187
CO | 15 | 30854.0678 | 6 | 28 |  | 0.0137
VOC (CH4) | 15 | 30854.0678 | 2 | 16 |  | 0.0026
NH3 | 15 | 30854.0678 | 5 | 17 |  | 0.0069
Convert Emission Limit (EL) in lb/MMBtu to Emission Factor in lb/MMscf, EF = EL x HHV (Btu/scf)
| Pollutant | EL | HHV | EF
|  | (lb/MMBtu) | (Btu/scf) | (lb/MMscf)
| NOx (NO2)/SCR | 0.0187 | 1050 | 19.64
| CO | 0.0137 | 1050 | 14.39
| VOC (CH4) | 0.0026 | 1050 | 2.73
| NH3 | 0.0069 | 1050 | 7.25
Emission Factors for PM10 and Sulfur Dioxide (SO2) all times
| Pollutant | Emission | HHV | Emission | Sulfur
|  | Factor | (Btu/scf) | Factor
|  | (lb/MMBtu) |  | (lb/MMscf) | (wt%)
| PM10 (5) | 0.0066 | 1050 | 6.93 | NA
| SO2 (5) | 0.94S | 1050 | 1.48 | 0.0015
Sulfur in Natural Gas (S)
WT% S = 100 x S in ppmv in natural gas x MW of S /(MW of Natural Gas x 106)
|  | Max.S in ppmv (4) | MW of S | MW of Natural Gas (2) | WT% S
|  | 8 | 32 | 17.2 | 0.0015
Exhaust Volume (WSCF/MMBtu) = 10,610 WSCF/MMBtu x 20.9/(20.9 -%O2) (9)(10)
Stack Gas Flow Rate, ACF = |  | Stack Gas Flow (SCF) x |  | [Stack Gas Temp (oR)]
[Standard Temp (oR)]
oR = oF + 460
Standard Temp = 60 oF
Unit | Oxygen | Exhaust Vol | Heat Input | Exhaust Flow | Stack Temp. | Exhaust Flow | Exhaust Flow
| (%) | (WSCF/MMBtu) | (MMBtu/hr) | (WSCFH) | (oF) | (WACFH) | (WACFS)
Ct#1, 0 - 10 hr | 15 | 37584.5763 | 126 | 4735657 | 824 | 11693430 | 3248
Ct#1, 11 - 60 hr | 15 | 37584.5763 | 266.7 | 10023806 | 824 | 24751090 | 6875
Ct#1, 61-84 hr | 15 | 37584.5763 | 409.5 | 15390884 | 824 | 38003644 | 10557
Unit | Stack Inside Diameter(11) | Stack Exit Velocity | Stack Exit Velocity | Stack Inside Diameter | Stack Height(11) | Stack Height
| (FT) | (FT/SEC) | (M/SEC) | (M) | (FT) | (M)
Ct#1, 0 - 10 hr | 10 | 41.35 | 12.6 | 3.05 | 110 | 33.53
Ct#1, 11 - 60 hr | 10 | 87.54 | 26.68 | 3.05 | 110 | 33.53
Ct#1, 61-84 hr | 10 | 134.42 | 40.97 | 3.05 | 110 | 33.53
(1) Specification provided by LA DWP from Request for Proposal dated September 25, 2000 and
S & S Energy Products' Specifications sheet.
(2) Information provided by LA DWP in an e-mail to Krishna Nand on 11/01/00.
(3) Specifications from LA DWP (Generation - 2000 Project Overview)
(4) SCR Bid specification (no. 9628) from LA DWP. Natural gas LHV calculated to be 953 Btu/scf.
(5) Taken from AP-42, Section 3.1. Emission factors are all load emission factors
AP-42 Combustion Turbine Emission Factor Development Document, Table 3.4-1.
PM10 and Sulfur Dioxide emission factor is from AP-42, Table 3.1-2a.
VOC emission factor based on manufacterer data since its value is higher than AP-42 uncontrolled factor.
NOx emissions for water injection based on GE guarantee of 25 ppmv.
(6) Taken from SCAQMD Title V Technical Guidance Manual, page A-20, 1998.
(7) EPA Method 19, 40 CFR Part 60.
(8) Emission Factor in lb/MMBtu is from AP-42, Table 3.1-1 and Table 3.1-2a.
(9) Taken from SCAQMD Title V Technical Guidance Manual, page A-20, 1998. Used natural gas F factor, wet.
(10) EPA Method 19, 40 CFR Part 60.
(11) Information regarding stack characteristics provided by DWP in an e-mail to Krishna Nand on 10/18/00.

## Air Toxics EF
CARB AIR TOXICS EMISSION FACTORS
COMBUSTION TURBINES -- NATURAL GAS
Air Toxics Emission factors are from California Air Resources Board's latest air toxics data
base. These emission factors are for combustion turbines equipped with SCR and CO
catalysts. The data were provided by CARB on 10/12/00 (fax from Kirk Rosenkranz to Krishna
Nand Tel. No. 916/322-7673).
Substance | Air Toxic | CAS No. | Rule 1401 | Mean Emission
Category |  |  | Listed Air | Factor
|  |  | Toxic (Y/N) | (lbs/MMSCF)
VOC | 1,3-Butadiene | 106990 | Y | 0.000127
SVOC | 2-Chloronaphthalene | 91587 | N | 2.72e-07
SVOC | 2-Methylnaphthalene | 91576 | N | 5.29e-06
PAH | Acenaphthene (PAH) | 83329 | N | 1.9e-05
PAH | Acenaphthylene (PAH) | 208968 | N | 1.47e-05
VOC | Acetaldehyde | 75070 | Y | 0.137
VOC | Acrolein | 107028 | Y | 0.0189
PAH | Anthracene (PAH) | 120127 | N | 3.38e-05
PAH | Benz(a)anthracene (PAH) | 56553 | Y | 2.26e-05
VOC | Benzene | 71432 | Y | 0.0133
PAH | Benzo(a)pyrene (PAH) | 50328 | Y | 1.39e-05
PAH | Benzo(b)fluoranthene (PAH) | 205992 | Y | 1.13e-05
PAH | Benzo(e)pyrene (PAH) | 192972 | N | 5.44e-07
PAH | Benzo(g,h,i)perylene (PAH) | 191242 | N | 1.37e-05
PAH | Benzo(k)fluoranthene (PAH) | 207089 | Y | 1.1e-05
PAH | Chrysene (PAH) | 218019 | Y | 2.52e-05
PAH | Dibenz(a,h)anthracene (PAH) | 53703 | Y | 2.35e-05
SVOC | Ethylbenzene | 100414 | Y | 0.0179
PAH | Fluoranthene (PAH) | 206440 | N | 4.32e-05
PAH | Fluorene (PAH) | 86737 | N | 5.8e-05
VOC | Formaldehyde | 50000 | Y | 0.917
VOC | Hexane | 110543 | Y | 0.259
PAH | Indeno(1,2,3-cd)pyrene (PAH) | 193395 | Y | 2.35e-05
PAH | Naphthalene (PAH) | 91203 | Y | 0.00166
SVOC | Perylene | 198550 | N | 7e-07
PAH | Phenanthrene (PAH) | 85018 | N | 0.000313
VOC | Propylene | 115071 | Y | 0.771
VOC | Propylene Oxide | 75569 | Y | 0.0478
PAH | Pyrene (PAH) | 129000 | N | 2.77e-05
VOC | Toluene | 108883 | Y | 0.071
VOC | Xylene(Total) | 1330207 | Y | 0.0261