## README (hidden)
Rev 1:
Corrected 8-hr CO startup modeling rate. Note: modeling was correct, since Rich caught this mistake when setting up runs
Rev 2; 12/7/06
Added BS ICE to EI for CEQA modeling
Corrected fuel use limits; updated LM6000 TACs to use new annual fuel use

## Criteria Emissions Summary
Table C.2.1
Mira Loma Site Facility-Wide Hourly, Daily, 30-Day, and Annual Emissions During Normal Operations | [11 empty] | modeled rates (g/s) | modeled rates (g/s)
Pollutant | Houly Uncontrolled Rate (1) (lb/hr) | Houly Controlled Rate (2) (lb/hr) | Maximum Daily Uncontrolled Rate (3) (lb/day) | Maximum Daily Controlled Rate (4) (lb/day) | 30-Day Average Rate (5) (lb/day) | Annual Average Rate (6) (lb/yr) | Annual Average Rate (7) (lb/yr) | Maximum Possible Hours at Normal Ops (hr) | daily final (lb/day) | w/out hr limit (lb/day) | CEQA threshold (lb/day) | 24-hr | 1-hr | 3-hr | 8-hr | 24-hr
NOx | 104.4038 | 8.8518 | 1136.5238 | 53.0918 | 23.867 | 7816.6849 | 7816.6849 | 12.9163 | 114.3325 | 101.9918 | 55 |  | 143.202 |  |  | 143.202
CO | 64.6159 | 10.1759 | 695.6159 | 73.7493 | 33.208 | 10839.4918 | 11009.7946 | 24 | 244.2226 | 150.3159 | 550 |  | 87.6476 |  | 87.6476 | 87.6476
PM10 | 4.5468 | 4.5468 | 49.696 | 49.696 | 22.7648 | 6666.3384 | 7650.0105 | 24 | 109.1227 | 108.3899 | 150 | 0.2609 |  |  |  | 6.2617
VOC | 2.3481 | 1.7783 | 21.5385 | 14.6368 | 6.5405 | 1919.4613 | 2190.0292 | 24 | 42.6785 | 31.149 | 55
SO2 | 0.25935 | 0.25935 | 2.834 | 2.834 | 1.2982 | 380.1441 | 436.2373 | 24 | 6.2244 | 6.1809 | 150 | 0.014878 | 0.35708 | 0.35708 |  | 0.35708
(1) Uncontrolled turbine emissions during commissioning.
(2) Startup hour.
(3) 1 hour of black start ICE operation and 11 hr/day operation of uncontrolled turbine emissions. | [7 empty] | 12 | <min daily hr limit rounded to single hour
(4) 1 hour of black start ICE operation, plus the sum of 1 startup hour, 1 shutdown hour, and 9 hours of fully controlled turbine operations. | [7 empty] | 11 | NOTE STARTUP IS CONTROLLING, SO LIMIT TO 11 HR/DAY
(5) 2 hours of black start ICE operation, plus daily controlled turbine emissions for 11 hr/day operation, for 30 days/month.
(6) Annual emissions for the first year with commissioning.
(7) Annual emissions for subsequent years following commissioning.

## TAC Emissions Summary
Table C.2.2
Mira Loma Site TAC Emissions Summary
Proposed Facility-Wide TAC Emissions During Normal Operations After Commissioning
Pollutant | CAS | MHU (lb/hr) | MHC (lb/hr) | MAC (lb/yr) | MAC (ton/yr)
1,3-Butadiene | 106-99-0 | 0.0013082 | 0.0013082 | 0.3283 | 0.00016415
Acetaldehyde | 75-07-0 | 0.018784 | 0.018784 | 29.0985 | 0.014549
Acrolein | 107-02-8 | 0.0029269 | 0.0029269 | 4.6547 | 0.0023273
Ammonia | 7664-41-7 | 3.1 | 3.1 | 5252.2857 | 2.6261
Benzene | 71-43-2 | 0.007104 | 0.007104 | 10.9128 | 0.0054564
Benzo(a)pyrene | 50-32-8 | 8.2671e-09 | 8.2671e-09 | 1.1574e-07 | 5.787e-11
Benzo(b)fluoranthene | 205-99-2 | 1.2523e-07 | 1.2523e-07 | 1.7532e-06 | 8.7662e-10
Benzo(g,h,i)perylene | 191-24-2 | 2.3087e-08 | 2.3087e-08 | 3.2321e-07 | 1.6161e-10
Benzo(k)fluoranthene | 207-08-9 | 2.3975e-08 | 2.3975e-08 | 3.3565e-07 | 1.6782e-10
Chrysene | 218-01-9 | 4.3785e-08 | 4.3785e-08 | 6.1299e-07 | 3.065e-10
Dibenz(a,h)anthracene | 53-70-3 | 8.2671e-09 | 8.2671e-09 | 1.1574e-07 | 5.787e-11
Ethylbenzene | 100-41-4 | 0.013949 | 0.013949 | 23.2637 | 0.011632
Formaldehyde | 50-00-0 | 0.31908 | 0.31908 | 516.2976 | 0.25815
Indeno(1,2,3-cd)pyrene | 193-39-5 | 2.1954e-08 | 2.1954e-08 | 3.0735e-07 | 1.5368e-10
Naphthalene | 91-20-3 | 0.00063468 | 0.00063468 | 0.94604 | 0.00047302
PAH [as benzo(a)pyrene] | 50-32-8 | 0.00094402 | 0.00094402 | 1.5992 | 0.00079958
Propylene | 115-07-1 | 0.016473 | 0.016473 | 0.23062 | 0.00011531
Propylene Oxide | 75-56-9 | 0.012444 | 0.012444 | 21.08 | 0.01054
Toluene | 108-88-3 | 0.056515 | 0.056515 | 94.5066 | 0.047253
Xylene | 1330-20-7 | 0.02944 | 0.02944 | 46.549 | 0.023274
|  |  | HAP Total (1) | 749.467 | 0.37473
(1) Ammonia is not a HAP and is not included in the HAP Total.
Note: LM6000 PAHs are listed as composite PAHs (as benzo[a]pyrene) in emission factor list; Black start generator
PAHs are speciated in emission factor database.

## Black Start Stack Parameters
Table C.2.3
Mira Loma Site Waukesha Black Start ICE Modeled Stack Parameters
Stack Height |  | Stack Temp. |  | Exhaust Flow | Stack Velocity |  | Stack Diam.
(ft) | (m) | (deg-F) | (K) | (acfm) | (ft/s) | (m/s) | (ft) | (m)
14.5 | 4.4207 | 843 | 723.7056 | 4694.2784 | 144.6011 | 44.0857 | 0.83 | 0.25305
Notes:
Stack height is 3 ft above 11.5 foot structure top.
Exhaust temp from Waukesha spec sheet for 645 KW capacity, 1800 rpm, standby power.
Exhaust flow rate calculated from Waukesha Heat Rejection and Operation Data spec sheet, and
Waukesha VGF36GL/GLD spec sheet. Flow rate reduced by factor of 29.1 inHg/29.54 inHg
average atmospheric pressure to account for 751 ft elevation.
Stack diameter verbal from Waukesha rep, 10/11/06 (10").

## LM6000 Stack Parameters
Table C.2.4
Mira Loma Site LM6000 Modeled Stack Parameters - Normal Operations
Stack Height |  | Stack Temp. |  | Exhaust Flow | Stack Velocity |  | Stack Diam.
(ft) | (m) | (deg-F) | (K) | (acfm) | (ft/s) | (m/s) | (ft) | (m)
80 | 24.3902 | 669 | 627.0389 | 478893.9864 | 60.1328 | 18.3332 | 13 | 3.9634
Notes:
Exhaust temp from "Catalyst Design (C06-135-GE Rev 2-Non Calc).xls", case 115.
Exhaust flow rate (ACFM) calculated from "406371 Guar Site 3 Mira Loma R1.pdf", and with correction
factor applied (in deg-R) to scale down the provided flow rate at 858.1F to 669F exhaust conditions.
Stack diameter from "SCE 5XLM600 - BOP Equipment Only_Aug 09 06.doc", page 6.
Table C.2.5
Mira Loma Site LM6000 Modeled Stack Parameters - Startup Conditions
Stack Height |  | Stack Temp. |  | Exhaust Flow | Stack Velocity |  | Stack Diam.
(ft) | (m) | (deg-F) | (K) | (acfm) | (ft/s) | (m/s) | (ft) | (m)
80 | 24.3902 | 669 | 627.0389 | 449841.0845 | 56.4848 | 17.221 | 13 | 3.9634
Notes:
Exhaust temp from "Catalyst Design (C06-135-GE Rev 2-Non Calc).xls", case 115.
Exhaust flow rate estimated for 12 minutes of startup from startup curve, with remaining 52 minutes at full load.
Stack diameter from "SCE 5XLM600 - BOP Equipment Only_Aug 09 06.doc", page 6.
Table C.2.6
Mira Loma Site LM6000 Modeled Stack Parameters - Commissioning
Stack Height |  | Stack Temp. |  | Exhaust Flow | Stack Velocity |  | Stack Diam.
(ft) | (m) | (deg-F) | (K) | (acfm) | (ft/s) | (m/s) | (ft) | (m)
80 | 24.3902 | 669 | 627.0389 | 239446.9932 | 30.0664 | 9.1666 | 13 | 3.9634
Notes:
Exhaust temp from "Catalyst Design (C06-135-GE Rev 2-Non Calc).xls", case 115.
Exhaust flow rate estimated to be 50% of full load during commissioning.
Stack diameter from "SCE 5XLM600 - BOP Equipment Only_Aug 09 06.doc", page 6.
Table C.2.7
Startup load factors by minute
factor of full load (1) | flow (ACFM) | minute
0 | 0 | 1
0 | 0 | 2
0 | 0 | 3
0 | 0 | 4
0 | 0 | 5
0 | 0 | 6
0.28 | 134090.3162 | 7
0.5 | 239446.9932 | 8
0.86 | 411848.8283 | 9
0.86 | 411848.8283 | 10
0.86 | 411848.8283 | 11
1 | 478893.9864 | 12
1 | 24902487.2917 | 13-60 < multiply flow rate times 52 minutes
| 449841.0845 | average flow rate during a startup hour
| 0.93933 | ratio of startup hour to a full load hour
(1) Based on startup curve.

## Black Start Criteria Pollutants
Mira Loma Site Waukesha Black Start ICE Calculations for Criteria Pollutants
Engine Specifications:
645 | KW
864.945 | bhp (KW * 1.341) | Assume no de-rating for elevation; Waukesha only provides de-rating values above 1,500 ft.
30 | minutes ICE operates during a black start/testing period
14 | number of black starts/testing hours per year
Table C.2.8
Data from Waukesha "Environmental Products 9" Spec Sheet: | [7 empty] | modeled rates (g/s)
Pollutant | Guaranteed Rate (g/bhp-hr) | Calculated Emission Rate (g/hr) | Maximum Houly Rate (1) (AHU/AHC/MHU/MHC) (lb/hr) | Maximum Daily Rate (2) (MDU/MDC) (lb/day) | 30-Day Average Rate (3) (30-DA) (lb/day) | Annual Average Rate (AA) (lb/yr) | PTE (tpy) | 1-hr | 3-hr | 8-hr | 24-hr | annual
NOx | 1.25 | 1081.1813 | 1.1918 | 1.1918 | 0.079452 | 16.6849 | 0.0083424 | 0.15016 |  |  |  | 0.00023999
CO | 1.59 | 1375.2625 | 1.5159 | 1.5159 | 0.10106 | 21.2232 | 0.010612 | 0.19101 |  | 0.023876
VOC (as NMHC) | 0.45 | 389.2253 | 0.42904 | 0.42904 | 0.028603 | 6.0066 | 0.0030033
(1) ICE will operate for 30 minutes, therefore calculated g/hr rate is
converted to lb/hr by dividing the rate by 30/60.
(2) Daily emission rates assume 1 black start or test in a day.
(3) 30-day average rates assume 2 hours of operation per month, consisting of 1 black start and 1 hour of testing.
Table C.2.9
AP-42 SO2 and PM10 Calculations (assume 4SLB):
Pollutant | Emission Factor (lb/MMBtu) | Rating (MMBtu/hr) | Maximum Houly Rate (1) (AHU/AHC/MHU/MHC) (lb/hr) | Maximum Daily Rate (2) (lb/day) | 30-Day Average Rate (3) (30-DA) (lb/day) | Annual Average Rate (AA) (lb/yr) | PTE (tpy)
SO2 | 0.000588 | 6.43 | 0.0018904 | 0.0018904 | 0.00012603 | 0.026466 | 1.3233e-05 | 0.00023819 | 7.9398e-05 |  | 9.9247e-06 | 3.8067e-07
PM10 | 0.00991 | 6.43 | 0.031861 | 0.031861 | 0.002124 | 0.44605 | 0.00022302 | 0.0040144 |  |  | 0.00016727 | 6.4158e-06
(1) ICE will operate for 30 minutes, therefore calculated g/hr rate is
converted to lb/hr by dividing the rate by 30/60.
(2) Daily emission rates assume 1 black start or test in a day.
(3) 30-day average rates assume 2 hours of operation per month, consisting of 1 black start and 1 hour of testing.
Notes: AP-42 assumes 2,000 gr/MMscf sulfur in natural gas for SO2 calculation.
PM10 emission factor represents condensible PM10.

## LM6000 Criteria SCAQMD styles
Table C.2.10
Mira Loma Site LM6000 Hourly, Daily, 30-Day, and Annual Emissions During Normal Operations | [11 empty] | modeled rates (g/s)
Pollutant | Houly Uncontrolled Rate (1) (AHU/MHU) (lb/hr) | Houly Controlled Rate (2) (AHC/MHC) (lb/hr) | Maximum Daily Uncontrolled Rate (3) (MDU) (lb/day) | Maximum Daily Controlled Rate (4) (MDC) (lb/day) | 30-Day Average Rate (5) (30-DA) (lb/day) | Annual Average Rate (6) (AA) (lb/yr) |  | Maximum Possible Hours at Normal Ops (hr) | daily final (lb/day) | w/out hr limit (lb/day) | CEQA threshold (lb/day) | 24-hr
NOx | 103.212 | 4.2 | 1135.332 | 46.2 | 21.175 | 7800 |  | 13.069 | 54.89 | 100.8 | 55
CO | 63.1 | 6.2 | 694.1 | 68.2 | 31.2583 | 10988.5714 |  | 24 | 148.8 | 148.8 | 550
PM10 | 4.5149 | 4.5149 | 49.6641 | 49.6641 | 22.7627 | 7649.5645 |  | 24 | 108.3581 | 108.3581 | 150 | 0.26074
VOC | 1.919 | 1.28 | 21.1094 | 14.08 | 6.4533 | 2184.0227 |  | 24 | 30.72 | 30.72 | 55
SO2 | 0.25746 | 0.25746 | 2.8321 | 2.8321 | 1.298 | 436.2108 |  | 24 | 6.179 | 6.179 | 150 | 0.014868
(1) AHU/MHU are uncontrolled emissions during commissioning.
(2) AHC/MHC are vendor guaranteed rates for NOx, CO, PM10, and VOC during normal operations. SO2 is AP-42 emission calculation.
(3) MDU calculated using MHU and 11 hr/day operation. | [7 empty] | 13 | <min daily hr limit rounded to single hour
(4) MDC calculated using MHC and 11 hr/day operation. | [7 empty] | NOTE: SU IS CONTROLLING SO 13 HRS NOT USED
(5) 30-DA calculated from MDC and 11 hr/day operation for 30 days/month.
(6) AA represents annual emissions for subsequent years following commissioning.
Table C.2.11
Mira Loma Site LM6000 Hourly, Daily, 30-Day, and Annual Emissions Including Startup and Shutdown Operations
Pollutant | Houly Uncontrolled Rate (1) (AHU/MHU) (lb/hr) | Houly Controlled Rate SU (2) (AHC/MHC) (lb/hr) | Houly Controlled Rate SD (3) (AHC/MHC) (lb/hr) | Maximum Daily Uncontrolled Rate (4) (MDU) (lb/day) | Maximum Daily Controlled Rate (5) (MDC) (lb/day) | 30-Day Average Rate (6) (30-DA) (lb/day) | Annual Average Rate (7) (AA) (lb/yr) | Maximum Possible Hours at Normal Ops (hr) | daily final (lb/day) | w/out hr limit (lb/day) | CEQA threshold (lb/day)
NOx | 103.212 | 7.66 | 6.44 | 1135.332 | 51.9 | 23.7875 | 7800 | 12.3696 | 94.751 | 106.5 | 55
CO | 63.1 | 8.66 | 7.7733 | 694.1 | 72.2333 | 33.1069 | 10988.5714 | 24 | 207.84 | 152.8333 | 550
PM10 | 4.5149 | 4.5149 | 4.5149 | 49.6641 | 49.6641 | 22.7627 | 7649.5645 | 24 | 108.3581 | 108.3581 | 150
VOC | 1.919 | 1.3492 | 1.3386 | 21.1094 | 14.2078 | 6.5119 | 2184.0227 | 24 | 32.3815 | 30.8478 | 55
SO2 | 0.25746 | 0.25746 | 0.25746 | 2.8321 | 2.8321 | 1.298 | 436.2108 | 24 | 6.179 | 6.179 | 150
(1) AHU/MHU are uncontrolled emissions during commissioning.
(2) AHC/MHC SU represent hourly average emission rates for a 12-minute startup, and 48 minutes of normal operations.
(3) AHC/MHC SD represent hourly average emission rates for an 8-minute shutdown, and 52 minutes of normal operations.
(4) MDU calculated using MHU and 11 hr/day operation. | [7 empty] | 12 | <min daily hr limit rounded to single hour
(5) MDC calculated as the sum of 1 startup hour, 1 shutdown hour, and 9 hours at normal operations. | [7 empty] | 11 | CALC DOESN'T WORK, SO ASSUME 11 HR/DAY
(6) 30-DA calculated from MDC and 11 hr/day operation for 30 days/month.
(7) AA represents annual emissions for subsequent years following commissioning.
Note: lead emission factors in AP-42 are non-detect for natural gas, therefore emissions of lead are negligible.

## LM6000 Criteria Hourly
Table C.2.12
Mira Loma Site LM6000 Hourly Emission Calculations During Normal Operations | [5 empty] | modeled rates (g/s)
Pollutant | Emission Factor | Emission Factor Units | Maximum Houly Rate (lb/hr) | Basis |  | 1-hr | 3-hr | 8-hr
NOx | n/a | n/a | 4.2 | Vendor Guarantee |  | 0.5292
CO | n/a | n/a | 6.2 | Vendor Guarantee |  | 0.7812 |  | 0.7812
PM10 | n/a | n/a | 4.5149 | Vendor Guarantee (2)
VOC | n/a | n/a | 1.28 | Vendor Guarantee
SO2 (1) | 0.0006 | lb/MMBtu | 0.25746 | AP-42 |  | 0.03244 | 0.03244
(1) AP-42, Section 3.1, Page 8, Supplement A.
(2) Vendor guarantee of 4.0 lb/hr, plus 2 times SO2 emission rate to account for estimated sulfates.
Table C.2.13
Mira Loma Site LM6000 Hourly Emission Calculations During Startup Conditions
Pollutant | Total Emissions During Startup (1) (lb) | Duration of Startup (min) | Maximum Houly Rate (2) (lb/hr) |  |  | 1-hr | 3-hr | 8-hr
NOx | 4.3 | 12 | 7.66 |  |  | 0.96516
CO | 3.7 | 12 | 8.66 |  |  | 1.0912 |  | 0.81995
PM10 | 0.90298 | 12 | 4.5149
VOC | 0.32523 | 12 | 1.3492
SO2 | 0.051492 | 12 | 0.25746 |  |  | 0.03244 | 0.010813
(1) NOx and CO totals during startup provided by vendor; VOC assumed to be uncontrolled for first 6.5 minutes;
Uncontrolled VOC emissions back-calculated assuming 33.3% control from oxidation catalyst;
PM10 and SO2 assumed equal to normal operations.
(2) Normal operation emissions assumed for 48 minutes after startup is complete.
Table C.2.14
Mira Loma Site LM6000 Hourly Emission Calculations During Shutdown Conditions
Pollutant | Total Emissions During Shutdown (1) (lb) | Duration of Shutdown (min) | Maximum Houly Rate (2) (lb/hr)
NOx | 2.8 | 8 | 6.44
CO | 2.4 | 8 | 7.7733
PM10 | 0.60199 | 8 | 4.5149
VOC | 0.22925 | 8 | 1.3386
SO2 | 0.034328 | 8 | 0.25746
(1) NOx and CO totals during shutdown provided by vendor; VOC assumed to be uncontrolled for last 5.5 minutes;
Uncontrolled VOC emissions back-calculated assuming 33.3% control from oxidation catalyst;
PM10 and SO2 assumed equal to normal operations.
(2) Normal operation emissions assumed for first 52 minutes of shutdown.
Table C.2.15
Mira Loma Site LM6000 Hourly Emission Calculations During Commissioning
Pollutant | Uncontrolled Commiss. Emissions (1) (lb/hr) | Duration of Uncontrolled Commissioning (hr) | Controlled Commiss. Emissions (2, 3) (lb/hr) | Duration of Controlled Commissioning (hr) | Total Commissioning Emissions (lb) | 1-hr | 3-hr | 8-hr
NOx | 103.212 | 5 | 42.3 | 20 | 1362.06 | 13.0047
CO | 63.1 | 5 | 63.1 | 20 | 1577.5 | 7.9506 |  | 7.9506
PM10 | 4.5149 | 5 | 4.5149 | 20 | 112.873
VOC | 1.919 | 5 | 1.919 | 20 | 47.976
SO2 | 0.25746 | 5 | 0.25746 | 20 | 6.4365 | 0.03244 | 0.03244
(1) Uncontrolled NOx calculated as water injection rate (42.3 lb/hr) times ratio of 61/25, where 61 = ppm "spike" on startup curve,
and 25 = ppm during water injection. Uncontrolled CO obtained from vendor guarantee spec sheet
("Catalyst Design (C06-135-GE Rev 2-Non Calc).xls"). Uncontrolled VOC emissions back-calculated assuming
33.3% control from oxidation catalyst.
(2) Hourly rates during normal operations assumed for PM10 and SO2.
(3) Water injection controlled emissions for NOx obtained from "Catalyst Design (C06-135-GE Rev 2-Non Calc).xls"); assumed no control
of CO and VOC from water injection.

## LM6000 Criteria Pollutant PTE
Table C.2.16
Mira Loma Site LM6000 PTE Calculations for Criteria Pollutants: First Year with Commissioning
Pollutant | Uncontrolled Commiss. Emissions (lb/hr) | Duration of Uncontrolled Commissioning (hr) | Water Injection Commiss. Emissions (lb/hr) | Duration of Water Injection Commissioning (hr) | SU (lb/hr) | SD (lb/hr) | Number of SU/SD Events | Normal Operations (lb/hr) | Hours at Normal Ops (hr) | PTE (tpy) | Maximum Possible Hours at Normal Ops (hr) | PTE (tpy) | PTE w/out Norm ops | PTE threshold
NOx | 103.212 | 5 | 42.3 | 20 | 7.66 | 6.44 | 60 | 4.2 | 1331.4143 | 3.9 | 1331.4143 | 3.9 | 1.104 | 4
CO | 63.1 | 5 | 63.1 | 20 | 8.66 | 7.7733 | 60 | 6.2 | 1331.4143 | 5.4091 | 8760 | 28.4378 | 1.2817 | 29
PM10 | 4.5149 | 5 | 4.5149 | 20 | 4.5149 | 4.5149 | 60 | 4.5149 | 1331.4143 | 3.3329 | 1582.6054 | 3.9 | 0.32733 | 4
VOC | 1.919 | 5 | 1.919 | 20 | 1.3492 | 1.3386 | 60 | 1.28 | 1331.4143 | 0.95673 | 5930.2777 | 3.9 | 0.10462 | 4
SO2 | 0.25746 | 5 | 0.25746 | 20 | 0.25746 | 0.25746 | 60 | 0.25746 | 1331.4143 | 0.19006 | 8760 | 1.1463 | 0.018666 | 4
Note: assumes that 60 SUs and 60 SDs occur separately during the year (60=120 events divided by 2 for 7/1/-12/31/07 operations)
Table C.2.17
Mira Loma Site LM6000 PTE Calculations for Criteria Pollutants: After Commissioning
Pollutant | SU (lb/hr) | SD (lb/hr) | Number of SU/SD Events | Normal Operations (lb/hr) | Hours at Normal Ops (hr) | PTE (tpy) |  |  |  |  | Maximum Possible Hours at Normal Ops (hr) | PTE (tpy) | PTE w/out Norm ops | PTE threshold | modeled rates (g/s)
NOx | 7.66 | 6.44 | 120 | 4.2 | 1454.2857 | 3.9 |  |  |  |  | 1454.2857 | 3.9 | 0.846 | 4 | 0.11219
CO | 8.66 | 7.7733 | 120 | 6.2 | 1454.2857 | 5.4943 |  |  |  |  | 8760 | 28.142 | 0.986 | 29
PM10 | 4.5149 | 4.5149 | 120 | 4.5149 | 1454.2857 | 3.8248 |  |  |  |  | 1487.6054 | 3.9 | 0.54179 | 4 | 0.11003
VOC | 1.3492 | 1.3386 | 120 | 1.28 | 1454.2857 | 1.092 |  |  |  |  | 5841.768 | 3.9 | 0.16127 | 4
SO2 | 0.25746 | 0.25746 | 120 | 0.25746 | 1454.2857 | 0.21811 |  |  |  |  | 8760 | 1.1586 | 0.030895 | 4 | 0.0062743
Note: assumes that 120 SUs and 120 SDs occur separately during the year

## LM6000 TACs
Table C.2.18
Mira Loma Site LM6000 TAC Emission Calculations
Assumptions:
Worst-Case Short-Term Turbine Fuel Use (Case 100 in GE specs)
fuel flow rate (MMBtu/hr) | 429.1 | HHV
Worst-Case Annual Turbine Fuel Use
fuel flow rate (MMBtu/yr) | 726895.4
Approx. Annual Operating Hours | 1694.2857
assumed fraction control from oxidation catalyst | 0
|  | AP-42 Emission Factor (1) | Emission Rate (2)
Pollutant | CAS | (lb/MMBtu) | MHU (lb/hr) | MHC (lb/hr) | MAC lb/yr | MAC ton/yr
1,3-Butadiene | 106-99-0 | 4.3e-07 | 0.00018451 | 0.00018451 | 0.31257 | 0.00015628
Acetaldehyde | 75-07-0 | 4e-05 | 0.017164 | 0.017164 | 29.0758 | 0.014538
Acrolein | 107-02-8 | 6.4e-06 | 0.0027462 | 0.0027462 | 4.6521 | 0.0023261
Benzene | 71-43-2 | 1.5e-05 | 0.0064365 | 0.0064365 | 10.9034 | 0.0054517
Ethylbenzene | 100-41-4 | 3.2e-05 | 0.013731 | 0.013731 | 23.2607 | 0.01163
Formaldehyde | 50-00-0 | 0.00071 | 0.30466 | 0.30466 | 516.0957 | 0.25805
Naphthalene | 91-20-3 | 1.3e-06 | 0.00055783 | 0.00055783 | 0.94496 | 0.00047248
PAH [as benzo(a)pyrene] | 50-32-8 | 2.2e-06 | 0.00094402 | 0.00094402 | 1.5992 | 0.00079958
Propylene Oxide | 75-56-9 | 2.9e-05 | 0.012444 | 0.012444 | 21.08 | 0.01054
Toluene | 108-88-3 | 0.00013 | 0.055783 | 0.055783 | 94.4964 | 0.047248
Xylene | 1330-20-7 | 6.4e-05 | 0.027462 | 0.027462 | 46.5213 | 0.023261
|  | HAP Total (3) | 0.44211 | 0.44211 | 748.9421 | 0.37447
Ammonia Slip (4)
Ammonia | 7664-41-7 | --- | 3.1 | 3.1 | 5252.2857 | 2.6261
Notes:
(1) AP-42 Section 3.1, Table 3.1-3 dated April 2000.
(2) 0% control from the oxidation catalyst was assumed for all toxics except ammonia for MHC.
(3) Ammonia is not a HAP and is not included in the HAP Total.
(4) Ammonia slip lb/hr rate from Express Integrated Technologies performance data for case #111;
Represents 5.0 ppm ammonia slip.

## Black Start TACs
Table C.2.19
Mira Loma Site Waukesha Black Start ICE TAC Emission Calculations using CATEF
Assumptions:
Worst-Case Short-Term ICE Use
fuel flow rate (MMBtu/hr) | 6.43
minutes/hour operation | 30 | minutes ICE operates during a black start/testing period
Annual Assumptions
Number of Black Starts/Testing Hours per year | 14
HHV of natural gas (btu/scf): | 1050
|  | CATEF Emission Factor (1) | Emission Rate
Pollutant | CAS | (lb/MMscf) | MHU (lb/hr) | MHC (lb/hr) | MAC (lb/yr) | MAC (ton/yr)
1,3-Butadiene | 106-99-0 | 0.367 | 0.0011237 | 0.0011237 | 0.015732 | 7.866e-06
Acetaldehyde | 75-07-0 | 0.529 | 0.0016197 | 0.0016197 | 0.022676 | 1.1338e-05
Acrolein | 107-02-8 | 0.059 | 0.00018065 | 0.00018065 | 0.0025291 | 1.2646e-06
Benzene | 71-43-2 | 0.218 | 0.0006675 | 0.0006675 | 0.0093449 | 4.6725e-06
Benzo(a)pyrene | 50-32-8 | 2.7e-06 | 8.2671e-09 | 8.2671e-09 | 1.1574e-07 | 5.787e-11
Benzo(b)fluoranthene | 205-99-2 | 4.09e-05 | 1.2523e-07 | 1.2523e-07 | 1.7532e-06 | 8.7662e-10
Benzo(g,h,i)perylene | 191-24-2 | 7.54e-06 | 2.3087e-08 | 2.3087e-08 | 3.2321e-07 | 1.6161e-10
Benzo(k)fluoranthene | 207-08-9 | 7.83e-06 | 2.3975e-08 | 2.3975e-08 | 3.3565e-07 | 1.6782e-10
Chrysene | 218-01-9 | 1.43e-05 | 4.3785e-08 | 4.3785e-08 | 6.1299e-07 | 3.065e-10
Dibenz(a,h)anthracene | 53-70-3 | 2.7e-06 | 8.2671e-09 | 8.2671e-09 | 1.1574e-07 | 5.787e-11
Ethylbenzene | 100-41-4 | 0.0711 | 0.0002177 | 0.0002177 | 0.0030478 | 1.5239e-06
Formaldehyde | 50-00-0 | 4.71 | 0.014422 | 0.014422 | 0.2019 | 0.00010095
Indeno(1,2,3-cd)pyrene | 193-39-5 | 7.17e-06 | 2.1954e-08 | 2.1954e-08 | 3.0735e-07 | 1.5368e-10
Naphthalene | 91-20-3 | 0.0251 | 7.6854e-05 | 7.6854e-05 | 0.001076 | 5.3798e-07
Propylene | 115-07-1 | 5.38 | 0.016473 | 0.016473 | 0.23062 | 0.00011531
Toluene | 108-88-3 | 0.239 | 0.0007318 | 0.0007318 | 0.010245 | 5.1226e-06
Xylene | 1330-20-7 | 0.646 | 0.001978 | 0.001978 | 0.027692 | 1.3846e-05
|  | HAP Total | 0.037491 | 0.037491 | 0.52487 | 0.00026244
(1) 4-Stroke, lean burn, >650 hp CATEF factors obtained 10/18/06.

## Indirect Emissions
Table C.2.20
2007 Motor Vehicle Exhaust Emission Factors
Passenger Vehicles (pounds/mile) |  | Delivery Trucks (pounds/mile)
CO | 0.01282 | CO | 0.0055203
NOx | 0.001361 | NOx | 0.035635
VOC | 0.001383 | VOC | 0.0012265
SOx | 9e-06 | SOx | 4.5721e-05
PM10 | 7.9948e-05 | PM10 | 0.00064407
Source: SCAQMD CEQA Analysis Guidance Handbook Web Site,
http://www.aqmd.gov/ceqa/hdbk.html
Note: The emission factors were compiled by running the California Air Resources Board's EMFAC2002
(version 2.2) Burden Model. A weighted average of vehicle types was used to calculate emission factors
for passenger vehicles, and emission factors for heavy heavy-duty diesel trucks were used for delivery trucks.
All the emission factors account for the emissions from start, running and idling exhaust. In addition, the VOC
emission factors take into account diurnal, hot soak, running and resting emissions, and PM10 emission factors
take into account tire and brake wear.
Vehicle Type | Exhaust Emission Factors
| CO (lb/mi) | VOC (lb/mi) | NOx (lb/mi) | SOx (lb/mi) | PM10 (lb/mi) | PM2.5 (lb/mi)a
On-Site Pickup Truck | 0.001361 | 9e-06 | 0.001383 | 7.9948e-05 | 0 | 0
Off-Site Dump Truck | 0.035635 | 4.5721e-05 | 0.0012265 | 0.00064407 | 0 | 0
Off-Site Concrete Truck | 0.035635 | 4.5721e-05 | 0.0012265 | 0.00064407 | 0 | 0
Off-Site Delivery Truck | 0.035635 | 4.5721e-05 | 0.0012265 | 0.00064407 | 0 | 0
Off-Site Construction Worker Commute | 0.001361 | 9e-06 | 0.001383 | 7.9948e-05 | 0 | 0
c PM2.5 emission factor [lb/hr] = PM10 emission factor [lb/hr] x PM2.5 fraction of PM10
PM2.5 Fraction of PM10 in Diesel Engine Exhaust = | 0.92 | from Final–Methodology to Calculate Particulate Matter (PM) 2.5
PM2.5 Fraction of PM10 in Gasoline Engine Exhaust = | 0.928 | and PM 2.5 Significance Thresholds, SCAQMD, October 2006
Emissions [pounds/day] = Emission factor [pounds/mile] x Vehicle miles traveled [miles/day]
Table C.2.21
Motor Vehicle Entrained Paved Road PM10 Emission Factors
Vehicle Type | On-Road Average Vehicle Weight (tons)a | Road Type | Silt Loading (g/m2)b | PM10 Emission Factor (lb/mi)c | PM2.5 Emission Factor (lb/mi)d
On-Site Pickup Truck | 2.7 | Local | 0.24 | 0.0034443 | 0
Off-Site Dump Truck | 2.7 | Collector | 0.037 | 0.0010216 | 0
Off-Site Concrete Truck | 2.7 | Collector | 0.037 | 0.0010216 | 0
Off-Site Delivery Truck | 2.7 | Collector | 0.037 | 0.0010216 | 0
Off-Site Construction Worker Commute | 2.7 | Collector | 0.037 | 0.0010216 | 0
a Weight of on-site vehicles based on vehicle class. Off-site average vehicle weight from
Methodology 7.9, Entrained Paved Road Dust (1997)
b From ARB Emission Inventory Methodology 7.9, Entrained Paved Road Dust (1997)
c Emission factor [g/mi] = 7.26 (Silt Loading/2)0.65 (Weight/3)1.5,
from ARB Emission Inventory Methodology 7.9, Entrained Paved Road Dust (1997)
d PM2.5 emission factor [lb/hr] = PM10 emission factor [lb/hr] x PM2.5 fraction of PM10
PM2.5 Fraction of PM10 in Paved Road Dust = | 0.169 | from Final–Methodology to Calculate Particulate Matter (PM) 2.5
and PM 2.5 Significance Thresholds, SCAQMD, October 2006
Emissions [pounds/day] = Emission factor [pounds/mile] x Vehicle miles traveled [miles/day]
Table C.2.22
Indirect Operational Emissions
Vehicle Type | One-way Miles | Emissions
|  | CO (lb) | VOC (lb) | NOx (lb) | SOx (lb) | PM10 (lb) | PM2.5 (lb)
Ammonia Delivery Truck | 30 | 2.1381 | 0.0027433 | 0.073591 | 0.038644 | 0.061297 | 0
Wastewater Delivery Truck | 0 | 0 | 0 | 0 | 0 | 0 | 0
Off-Site Construction Worker Commute | 30 | 0.08166 | 0.00054 | 0.08298 | 0.0047969 | 0.061297 | 0
Total |  | 2.2197 | 0.0032833 | 0.15657 | 0.043441 | 0.12259 | 0

## Supplemental Info
Mira Loma Site Support Calculations
LM6000 Fuel Use
429.1 | MMBtu/hr (HHV)
429100000 | Btu/hr (HHV)
1050 | HHV btu/scf conversion
408666.6667 | scf/hr | using MMBtu
408666.6667 | scf/hr | using Btu
First Year with Commissioning Annual Fuel use:
603361304.7619 | scf/yr | Calced using scf/hr * annual op hours below
1476.4143 | hr/yr | Calced from LM6000 Criteria Pollutant PTE sheet for normal ops (1331 hr/yr), plus 60 hr for SU plus 60 hr for SD plus 25 hr for commiss.
Subsequent Years after Commissioning Annual Fuel use:
692398095.2381 | scf/yr | Calced using scf/hr * annual op hours below
1694.2857 | hr/yr | Calced from LM6000 Criteria Pollutant PTE sheet for normal ops (1454 hr/yr), plus 120 hr for SU plus 120 hr for SD
Waukesha ICE Fuel Use
6.43 | MMBtu/hr
6430000 | Btu/hr
1050 | HHV btu/scf conversion
6123.8095 | scf/hr | using MMBtu
6123.8095 | scf/hr | using Btu
85733.3333 | scf/yr < assume 14 hr/yr ops
Facility-Wide Fuel Use: Subsequent Years after Commissioning
414790.4762 | total hourly fuel use (scf/hr)
692483828.5714 | total annual fuel use (scf/yr)
4501457.1429 | total daily fuel use (scf/day) calced from LM6000 daily normal op hours (11 hr/day), plus 1 hour for black start per day
PM emission limit compliance demonstration for turbine
4.5149 | lb/hr emission rate
429.1 | MMBtu/hr (HHV)
0.010522 | lb/MMBtu
PM emission limit compliance demonstration for ICE
0.031861 | lb/hr emission rate
6.43 | MMBtu/hr (HHV)
0.004955 | lb/MMBtu

## CATEF ICE FACTORS (hidden)
ID | System | Material | SCC | APC | Other | CAS | Substance | Max | Mean | Median | Unit
| Type | Type |  | Device | Description |  |  | Emission
factor
3458 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 106-99-0 | 1,3-Butadiene | 0.415 | 0.367 | 0.378 | lbs/MMcf
3462 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 75-07-0 | Acetaldehyde | 2.62 | 0.529 | 0.0392 | lbs/MMcf
3465 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 107-02-8 | Acrolein | 0.161 | 0.059 | 0.0392 | lbs/MMcf
3469 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 71-43-2 | Benzene | 0.259 | 0.218 | 0.212 | lbs/MMcf
3471 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 50-32-8 | Benzo(a)pyrene | 3.88e-06 | 2.7e-06 | 2.52e-06 | lbs/MMcf
3472 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 205-99-2 | Benzo(b)fluoranthene | 7.98e-05 | 4.09e-05 | 3.49e-05 | lbs/MMcf
3473 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 191-24-2 | Benzo(g,h,i)perylene | 1.71e-05 | 7.54e-06 | 6.81e-06 | lbs/MMcf
3474 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 207-08-9 | Benzo(k)fluoranthene | 1.21e-05 | 7.83e-06 | 8.54e-06 | lbs/MMcf
3475 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 218-01-9 | Chrysene | 2.25e-05 | 1.43e-05 | 1.58e-05 | lbs/MMcf
3476 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 53-70-3 | Dibenz(a,h)anthracene | 3.88e-06 | 2.7e-06 | 2.52e-06 | lbs/MMcf
3477 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 100-41-4 | Ethylbenzene | 0.115 | 0.0711 | 0.07 | lbs/MMcf
3482 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 50-00-0 | Formaldehyde | 20.9 | 4.71 | 0.365 | lbs/MMcf
3483 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 193-39-5 | Indeno(1,2,3-cd)pyrene | 1.09e-05 | 7.17e-06 | 8.06e-06 | lbs/MMcf
3484 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 91-20-3 | Naphthalene | 0.031 | 0.0251 | 0.0234 | lbs/MMcf
3487 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 115-07-1 | Propylene | 12.1 | 5.38 | 4.25 | lbs/MMcf
3490 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 108-88-3 | Toluene | 0.394 | 0.239 | 0.259 | lbs/MMcf
3491 | Internal Combustion Engine | Natural gas | 20200202 | None | 4S/Lean/>650Hp | 1330-20-7 | Xylene | 0.965 | 0.646 | 0.685 | lbs/MMcf