## Cost worksheet SOR
| Value | Units
Input Value and Units | 1000 | SCFM
Biogas Higher Heating Value (HHV) | 500 | Btu/ft3
Engine Efficiency | 32 | %
Inlet Flow Rate | 1000 | SCFM
Engine Power | 2813.4762 | kW
Engine Power | 3772.9331 | bhp
SILOXANE-ONLY REMOVAL (SOR) SYSTEM CAPITAL AND ANNUAL COSTS CALCULATOR
Cost Items | Cost Factors | Factor | Removal System Cost ($) | Default Factor
DIRECT CAPITAL COSTS (DCC):
(1) Siloxane Removal System Equipment Cost (SRSEC) | Calculated by program |  | 467585.955
(2) Auxiliary Equipment | 5% of equipment cost (SRSEC) | 5% | 23379.2977 | 5%
(3) Freight | 5% of SRSEC | 5% | 23379.2977 | 5%
(4) Sales Tax | 10% of (SRSEC+auxiliary+freight) | 10% | 46758.5955 | 10%
Subtotal: Total Equipment Cost (TEC) | (1) + (2) + (3) + (4) |  | 561103.146
(3) Direct Installation Costs
(a) Foundation and Structural Support | 8% of TEC | 8% | 44888.2517 | 8%
(b) Handling & Erection | 14% of TEC | 14% | 78554.4404 | 14%
(c) Electrical | 4% of TEC | 4% | 22444.1258 | 4%
(d) Piping | 2% of TEC | 2% | 11222.0629 | 2%
(e) Insulation | 1% of TEC | 1% | 5611.0315 | 1%
(f) Painting | 1% of TEC | 1% | 5611.0315 | 1%
Subtotal: Total Direct Installation Costs (DIC) | (a) + (b) + (c) + (d) + (e) + (f) |  | 168330.9438
Total DCC: | TEC + DIC |  | 729434.0898
INDIRECT CAPITAL COSTS (ICC):
(1) Indirect Installation Costs (IIC)
(a) General Facilities | 5% of TEC | 5% | 28055.1573 | 5%
(b) Engineering and Home Office Fees | 10% of TEC | 10% | 56110.3146 | 10%
(c) Process Contingency | 10% of TEC | 10% | 56110.3146 | 10%
(2) Other Indirect Costs (OIC)
(a) Siloxane Monitor | Engineering Estimate | 75000 | 75000 | 75000
(b) Startup and Performance Testing | 1% of TEC | 1% | 5611.0315 | 1%
(c) Spare Parts | 1% of TEC | 1% | 5611.0315 | 1%
(d) Contractor Fees | 10% of TEC | 10% | 56110.3146 | 10%
Total ICC: | IIC+OIC |  | 282608.164
PROJECT CONTINGENCY | 15% of (DCC+ICC) | 15% | 151806.3381 | 15%
RETROFIT COSTS | 0% of TIC | 0% | 0 | 0%
TOTAL CAPITAL INVESTMENT (TCI): | DCC+ICC+Project Contingency+Retrofit Costs |  | 1163848.5918
DIRECT OPERATING COSTS (DOC):
(1) Operating Labor
(a) Operator |  |  | 21900
hr/shift |  | 0.5 |  | 0.5
Pay Rate |  | 40 |  | 40
Operating Hours |  | 8760 |  | 8760
(b) Supervisor | 15% of operator cost | 15% | 3285 | 15%
(2) Maintenance (labor and material) | 1.5% of TCI | 1.5% | 17457.7289 | 1.5%
(3) Siloxane Removal System Media Replacement + Energy Requirement | Calculated by program |  | 32174.9472
(4) Siloxane System Periodic Testing | Engineering estimate | 24000 | 24000 | 24000
Total DOC: | (a) + (b) + (2) + (3) + (4) |  | 98817.6761
INDIRECT OPERATING COSTS (IOC):
(1) Overhead | 60% of (operator labor (1) + maintenance (2)) | 60% | 25585.6373 | 60%
(2) Property Taxes | 1% of total capital investment | 1% | 11638.4859 | 1%
(3) Insurance | 1% of total capital investment | 1% | 11638.4859 | 1%
(4) Administration | 2% of total capital investment | 2% | 23276.9718 | 2%
(5) Capital recovery costs (CRC) | CRF x TCI |  | 165732.0395
Capital recovery factor (CRF) | 0.1424
Interest rate |  | 7% |  | 7%
Annualization years |  | 10 |  | 10
Total IOC: | (1) + (2) + (3) + (4) + (5) |  | 237871.6205
Recovery Credits (RC) | Engineering Estimate | 0 | 0 | 0
TOTAL ANNUAL COST (TAC): | DOC + IOC - RC |  | 336689.2965
TOTAL ANNUAL COST PER kWh |  |  | 0.013661
TOTAL ANNUAL COST PER MMBtu |  |  | 1.2812
TOTAL ANNUAL COST PER MSCF |  |  | 0.64058
Note on D5: Input either flowrate or engine power.
Note on E5: Input either SCFM, kW or BHP.

## Cost worksheet ACR
| Value | Units
Input Value and Units | 1000 | SCFM
Biogas Higher Heating Value (HHV) | 500 | Btu/ft3
Engine Efficiency | 32 | %
Inlet Flow Rate | 1000 | SCFM
Engine Power | 2813.4762 | kW
Engine Power | 3772.9331 | bhp
ALL-CONTAMINANTS REMOVAL (ACR) SYSTEM CAPITAL AND ANNUAL COSTS CALCULATOR
Cost Items | Cost Factors | Factor | Removal System Cost ($) | Default Factor
DIRECT CAPITAL COSTS (DCC):
(1) Siloxane Removal System Equipment Cost (SRSEC) | Calculated by program |  | 2376874
(2) Auxiliary Equipment | 5% of equipment cost (SRSEC) | 5% | 118843.7 | 5%
(3) Freight | 5% of equipment cost (SRSEC) | 5% | 118843.7 | 5%
(4) Sales Tax | 10% of (equipment(SRSEC)+freight) | 10% | 237687.4 | 10%
Subtotal: Total Equipment Cost (TEC) | (1) + (2) + (3) + (4) |  | 2852248.8
(3) Direct Installation Costs
(a) Foundation and Structural Support | 8% of TEC | 8% | 228179.904 | 8%
(b) Handling & Erection | 14% of TEC | 14% | 399314.832 | 14%
(c) Electrical | 4% of TEC | 4% | 114089.952 | 4%
(d) Piping | 2% of TEC | 2% | 57044.976 | 2%
(e) Insulation | 1% of TEC | 1% | 28522.488 | 1%
(f) Painting | 1% of TEC | 1% | 28522.488 | 1%
Subtotal: Total Direct Installation Costs (DIC) | (a) + (b) + (c) + (d) + (e) + (f) |  | 855674.64
Total DCC: | TEC + DIC |  | 3707923.44
INDIRECT CAPITAL COSTS (ICC):
(1) Indirect Installation Costs (IIC)
(a) General Facilities | 5% of TEC | 5% | 142612.44 | 5%
(b) Engineering and Home Office Fees | 10% of TEC | 10% | 285224.88 | 10%
(c) Process Contingency | 10% of TEC | 10% | 285224.88 | 10%
(2) Other Indirect Costs (OIC)
(a) Siloxane Monitor | Engineering Estimate | 75000 | 75000 | 75000
(b) Startup and Performance Testing | 1% of TEC | 1% | 28522.488 | 1%
(c) Spare Parts | 1% of TEC | 1% | 28522.488 | 1%
(d) Contractor Fees | 10% of TEC | 10% | 285224.88 | 10%
Total ICC: | IIC+OIC |  | 1130332.056
PROJECT CONTINGENCY | 15% of (DCC+ICC) | 15% | 725738.3244 | 15%
RETROFIT COSTS | 0% of TIC | 0% | 0 | 130%
TOTAL CAPITAL INVESTMENT (TCI): | DCC+ICC+Project Contingency+Retrofit Costs |  | 5563993.8204
DIRECT OPERATING COSTS (DOC):
(1) Operating Labor
Operator |  |  | 21900
hr/shift |  | 0.5 |  | 0.5
Pay Rate |  | 40 |  | 40
Operating Hours |  | 8760 |  | 8760
Supervisor | 15% of operator cost | 15% | 3285 | 15%
(2) Maintenance (labor and material) | 1.5% of TCI | 1.5% | 83459.9073 | 1.5%
(3) Siloxane Removal System Media Replacement + Energy Requirement | Calculated by program |  | 219709.6546
(4) Siloxane system periodic testing | Engineering estimate | 24000 | 24000 | 24000
Total DOC: | (a) + (b) + (2) + (3) + (4) |  | 352354.5619
INDIRECT OPERATING COSTS (IOC):
(1) Overhead | 60% of (operator labor + maintenance) | 60% | 65186.9444 | 60%
(2) Property Taxes | 1% of total capital investment | 1% | 55639.9382 | 1%
(3) Insurance | 1% of total capital investment | 1% | 55639.9382 | 1%
(4) Administration | 2% of total capital investment | 2% | 111279.8764 | 2%
(5) Capital recovery costs (CRC) | CRF x TCI |  | 792312.72
Capital recovery factor (CRF) | 0.1424
Interest rate |  | 7% |  | 7%
Annualization years |  | 10 |  | 10
Total IOC: | (1) + (2) + (3) + (4) + (5) |  | 1080059.4172
Recovery Credits (RC) | Engineering Estimate | 0 | 0 | 0
TOTAL ANNUAL COST (TAC): | DOC + IOC-RC |  | 1432413.9791
TOTAL ANNUAL COST PER kWh |  |  | 0.058119
TOTAL ANNUAL COST PER MMBtu |  |  | 5.4506
TOTAL ANNUAL COST PER MSCF |  |  | 2.7253
Note on E5: Input either flowrate or engine power.
Note on F5: Input either SCFM, kW or BHP.

## Factors&Regression equations
Least Squares Regression Equations
| LS Equation | m | b
Equipment Costs (all-contaminants removal, ACR) | y=mx+b | 1741.5 | 635374
Equipment Costs (siloxane-only removal, SOR) | y=mxb | 35064 | 0.375
O&M Costs (all-contaminants, ACR) | y=mxb | 306.09 | 0.952
O&M Costs (siloxane-only, SOR) | y=mxb | 2047 | 0.3988
Cost Factor Ranges
Total Equipment Costs (TEC) | Range, %
Purchased equipment costs
Auxiliary Equipment | 10-50
Sales taxes | 0-8
Freight | 1-10
Purchased equipment cost, PEC
Direct Installation Costs (DIC)
Foundations & supports | 4-12
Handling & erection | 14-50
Electrical | 1-8
Piping | 2-30
Insulation | 1-7
Painting | 1-10
Direct installation costs
Total Direct Costs (TDC)
Indirect Installation Costs (IIC)
Engineering | 10-20
Construction and field expenses | 5-20
Contractor fees | 0-10
Start-up | 1-2
Model study | 2-3
Performance test | 1
Contingencies | 3
Retrofit Costs | 10-50

## Engine maintenance savings
Category | Siloxane Level, ppmv | Payback Years
Moderate | 0.5 - <9 | 3
Heavy | >9 - <25 | 2
Severe | >25 - <60 | 1
Extreme | >60 - 140+ | 0.5
Savings Include (based on siloxane levels)
Spark plugs: increase life 3x to 4x
Engine re-build from 5,000 to 40,000 hours
Exhaust heat boiler re-tube: increase life by 3x to 4x
Power Savings / Availability: increase of 75 to 92%
Oil changes increase interval: 500 to 1,440 hours
Pre-chamber and prechamber check valve by 2x to 6x
Assumptions-
1. Gas already meets engine OEM gas cleanliness standards
2. Lean Burn Engines